{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["DGDG柴油发电机","DGCU柴发控制箱"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"DGDG柴油发电机","index":0,"n_rows":79,"n_cols":10,"rows_kept":79,"cut":false,"hidden":false,"merged":[[77,0,77,1],[78,0,78,1],[0,0,0,9],[1,0,1,1],[40,1,66,1],[72,1,76,1],[40,0,76,0],[2,0,39,0],[30,1,39,1],[67,1,71,1],[2,1,29,1]]}
["柴油发电机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","发电机组","额定输出电压","RatedOutU","kV","Num","S","A2"]
[null,null,"额定输出电流","RatedOutI","A","Num","M","A2"]
[null,null,"额定输出功率","RatedOutP","kW","Num","S","A2"]
[null,null,"额定发电频率","RatedOutFreq","Hz","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","M","A2"]
[null,null,"额定功率因数","RatedPFactor",null,"Num","R","A1",null,"电压与电流之间的相位差(Φ)的余弦叫做功率因数"]
[null,null,"满载燃油耗量","FullLoadDieselConsum","L/kWh","Num","M","A2"]
[null,null,"稳态电压调整率","StableUAdjustRate","%","Num","R","A2",null,"变压器某一个绕组的空载电压和同一绕组在规定负载和功率因数时的电压之差与该绕组空载电压的比"]
[null,null,"瞬态电压调整率","UAdjustRate","%","Num","R","A2",null,"一次电压保持不变，在某一个负载性质（功率因数）某一个负载电流时，二次的空载电压U1与负载电压U2之差除以空载电压U1的百分数"]
[null,null,"电压波动率","UVolatility","%","Num","R","A2",null,"波动的电压值与当时的电压之比"]
[null,null,"电压波形失真度","UWaveDistortion","%","Num","R","A2"]
[null,null,"电压稳定时间","UStableTime","s","Num","R","A2",null,"从开始运行到电压稳定的时间"]
[null,null,"稳态频率调整率","StableFreqAdjustRate","%","Num","R","A2",null,"负载变化前后，机组稳定频率的差值与额定频率之比的百分数。稳态频率调整率越小，说明负载变化时频率越稳定"]
[null,null,"瞬态频率调整率","FreqAdjustRate","%","Num","R","A2",null,"发电机组在突加或突减负载时，瞬间变化频率与负载变化前频率的差值与额定频率的比值"]
[null,null,"频率波动率","FreqVolatility","%","Num","R","A2"]
[null,null,"频率稳定时间","FreqStableTime","s","Num","R","A2",null,"从开始运行到频率稳定的时间"]
[null,null,"接线方式","ConnectType",null,"Str","R","B1",null,"一般为三相四线"]
[null,null,"抗震能力","SeismicCapacity",null,"Enum","S","D1","参考《10抗震设防烈度》"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"柴油机","额定功率","RatedP","kW","Num","R","A2"]
[null,null,"气缸数","CylinderNum","个","Num","R","A2"]
[null,null,"缸径","CylinderDiameter","mm","Num","R","A2"]
[null,null,"行程","Stroke","mm","Num","R","A2"]
[null,null,"排气量","Displacement","L","Num","R","A2"]
[null,null,"柴油容量","DieselCap","L","Num","R","A2"]
[null,null,"润滑油容量","LubeCap","L","Num","R","A2"]
[null,null,"冷却方式","CoolType",null,"Enum","R","D1","1. 风冷 2. 水冷 99. 其他"]
[null,null,"进气方式","GasInType",null,"Enum","R","D1","1. 自然吸气 2. 废气涡轮增压 99. 其他"]
[null,null,"调速方式","SpeedCtrlType",null,"Enum","R","D1","1. 电子调速 2. 机械调速 99. 其它"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相输出电压","APhaseOutU","kV","Inst","R","L"]
[null,null,"B相输出电压","BPhaseOutU","kV","Inst","R","L"]
[null,null,"C相输出电压","CPhaseOutU","kV","Inst","R","L"]
[null,null,"A相输出电流","APhaseOutI","A","Inst","R","L"]
[null,null,"B相输出电流","BPhaseOutI","A","Inst","R","L"]
[null,null,"C相输出电流","CPhaseOutI","A","Inst","R","L"]
[null,null,"A相输出有功功率","APhaseOutActiveP","kW","Inst","R","L"]
[null,null,"B相输出有功功率","BPhaseOutActiveP","kW","Inst","R","L"]
[null,null,"C相输出有功功率","CPhaseOutActiveP","kW","Inst","R","L"]
[null,null,"总输出有功功率","TotOutActiveP","kW","Inst","M","L"]
[null,null,"A相输出无功功率","APhaseOutReactiveP","kVar","Inst","R","L"]
[null,null,"B相输出无功功率","BPhaseOutReactiveP","kVar","Inst","R","L"]
[null,null,"C相输出无功功率","CPhaseOutReactiveP","kVar","Inst","R","L"]
[null,null,"总输出无功功率","TotOutReactiveP","kVar","Inst","R","L"]
[null,null,"A相输出视在功率","APhaseOutApparentP","kVA","Inst","R","L"]
[null,null,"B相输出视在功率","BPhaseOutApparentP","kVA","Inst","R","L"]
[null,null,"C相输出视在功率","CPhaseOutApparentP","kVA","Inst","R","L"]
[null,null,"总输出视在功率","TotOutApparentP","kVA","Inst","M","L"]
[null,null,"输出频率","OutFreq","Hz","Inst","R","L"]
[null,null,"逐时耗燃油量","DieselConsumP","L/h","Inst","M","L"]
[null,null,"油箱储量","DieselStore","L","Inst","R","L"]
[null,null,"机内润滑油量","LubeStore","L","Inst","R","L"]
[null,"关键指标","A相输出功率因数","APhasePFactor",null,"Inst","R","M"]
[null,null,"B相输出功率因数","BPhasePFactor",null,"Inst","R","M"]
[null,null,"C相输出功率因数","CPhasePFactor",null,"Inst","R","M"]
[null,null,"总输出功率因数","TotPFactor",null,"Inst","R","M"]
[null,null,"单位发电量油耗","UnitEDieselConsum","L/kWh","Inst","R","M"]
[null,"累计指标","累计发电量","AccOutE","kWh","Acc","R","M"]
[null,null,"累计耗油量","AccDieselConsum","L","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"DGCU柴发控制箱","index":1,"n_rows":61,"n_cols":10,"rows_kept":61,"cut":false,"hidden":false,"merged":[[60,0,60,1],[59,0,59,1],[0,0,0,9],[1,0,1,1],[2,0,48,0],[49,0,58,0],[49,1,53,1],[54,1,58,1],[18,1,48,1],[2,1,17,1]]}
["控制箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","额定输入电压","RatedInputU","V","Num","R","A2"]
[null,null,"额定输出电压","RatedOutputU","V","Num","R","A2"]
[null,null,"应答时间","ResponseTime","ms","Num","M","A2"]
[null,null,"允许瞬时断电时间","AllowPowerOffTime ","ms","Num","M","A2"]
[null,null,"是否有网络功能","isNetwork",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"IP地址","IPAddress",null,"Str","S","B1"]
[null,null,"子网掩码","SubnetMask",null,"Str","S","B1"]
[null,null,"网关","Gateway",null,"Str","S","B1"]
[null,null,"DNS服务器地址","DNS",null,"Str","S","B1"]
[null,null,"适用网络类型","NetType",null,"Enum","M","D1","1. 千兆以太网 2. 万兆以太网 3. 光纤 99. 其他"]
[null,null,"传输速率","TransferSpeed","MB/s","Num","M","A2"]
[null,null,"主芯片类型","MainChip",null,"Str","R","B1"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,"接口","输入485接口数量","In485PortNum","个","Num","R","A2"]
[null,null,"输出485接口数量","Out485PortNum","个","Num","R","A2"]
[null,null,"输入232接口数量","In232PortNum","个","Num","R","A2"]
[null,null,"输出232接口数量","Out232PortNum","个","Num","R","A2"]
[null,null,"输入422接口数量","In422PortNum","个","Num","R","A2"]
[null,null,"输出422接口数量","Out422PortNum","个","Num","R","A2"]
[null,null,"输入MBUS接口数量","InMBUSPortNum","个","Num","R","A2"]
[null,null,"输出MBUS接口数量","OutMBUSPortNum","个","Num","R","A2"]
[null,null,"输入音频接口数量","InAudioPortNum","个","Num","R","A2"]
[null,null,"输出音频接口数量","OutAudioPortNum","个","Num","R","A2"]
[null,null,"HDMI接口数量","HDMIPortNum","个","Num","R","A2"]
[null,null,"VGA接口数量","VGAPortNum","个","Num","R","A2"]
[null,null,"USB接口数量","USBPortNum","个","Num","R","A2"]
[null,null,"以太网接口数量","EthernetPortNum ","个","Num","R","A2"]
[null,null,"光纤接口数量","FiberPortNum ","个","Num","R","A2"]
[null,null,"电压AI接口数量","AIUPortNum","个","Num","R","A2"]
[null,null,"电压AI信号","AIU","V","Num","R","A2"]
[null,null,"电流AI接口数量","AIIPortNum","个","Num","R","A2"]
[null,null,"电流AI信号","AII","A","Num","R","A2"]
[null,null,"电压AO接口数量","AOUPortNum","个","Num","R","A2"]
[null,null,"电压AO信号","AOU","V","Num","R","A2"]
[null,null,"电流AO接口数量","AOIPortNum","个","Num","R","A2"]
[null,null,"电流AO信号","AOI","A","Num","R","A2"]
[null,null,"DI干节点接口数量","DIDryNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点接口数量","DIWetNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点电压","DIWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"DO干节点接口数量","DODryNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点接口数量","DOWetNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点电压","DOWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"输入同轴线接口数量","InCoaxialPortNum","个","Num","R","A2"]
[null,null,"输出同轴线接口数量","OutCoaxialPortNum","个","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"在线状态","OnlineStatus",null,"Boolv","S","L","0. 脱线 1. 在线"]
[null,null,"上传速度","UploadSpeed","MB/s","Inst","R","L"]
[null,null,"下载速度","DownloadSpeed","MB/s","Inst","R","L"]
[null,"累计指标","累计上传数据量","AccUploadData","GB","Acc","R","L"]
[null,null,"累计下载数据量","AccDownloadData","GB","Acc","R","L"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","L"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","L"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]