{"text_format":"2","workbook":"xlsx","n_sheets":21,"sheets":["FSHP消火栓供水加压泵","FSSP喷淋供水加压泵","FSMP水喷雾供水加压泵","FSAP停机坪消防供水加压泵","FSWM消防水炮设备","FSPS消防稳压设备","FSFT泡沫储罐组","FSAC消防空压机","FSWV湿式报警阀组","FSDV干式报警阀组","FSPV预作用报警阀组","FSHB消火栓箱","FSOH室外消火栓","FSPC消防水泵接合器","FSTC消防伴热电缆","FSET消防末端试水装置","FSWT消防水箱","FSFP消防补水泵","FSSN消防喷头","FSCP消火栓控制面板","FSCU消防给水控制箱"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"FSHP消火栓供水加压泵","index":0,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[73,0,76,1],[77,0,77,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[67,1,72,1],[1,0,1,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"水泵出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"水泵出口压力报警","OutPressAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"FSSP喷淋供水加压泵","index":1,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[73,0,76,1],[77,0,77,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[67,1,72,1],[1,0,1,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"水泵出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"水泵出口压力报警","OutPressAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"FSMP水喷雾供水加压泵","index":2,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[73,0,76,1],[77,0,77,1],[67,1,72,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"水泵出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"水泵出口压力报警","OutPressAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"FSAP停机坪消防供水加压泵","index":3,"n_rows":78,"n_cols":10,"rows_kept":78,"cut":false,"hidden":false,"merged":[[73,0,76,1],[77,0,77,1],[67,1,72,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S","L","0. 停止 1. 运行"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S","L"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"水泵出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"水泵出口压力报警","OutPressAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"FSWM消防水炮设备","index":4,"n_rows":41,"n_cols":10,"rows_kept":41,"cut":false,"hidden":false,"merged":[[39,0,39,1],[40,0,40,1],[24,0,38,0],[0,0,0,9],[1,0,1,1],[24,1,33,1],[34,1,38,1],[2,0,23,1]]}
["消防水炮设备"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","M","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","M","A2"]
[null,null,"额定出口流量","RatedOutFlow","m3/h","Num","S","A2"]
[null,null,"额定出口压力","RatedOutPress","MPa","Num","S","A2"]
[null,null,"额定射程","RatedRange","m","Num","S","A2"]
[null,null,"水平回转角度","HorizontalRotateAngle","°","Num","M","A2"]
[null,null,"最大仰角","MaxElevationAngle","°","Num","M","A2"]
[null,null,"最小俯角","MinDepressionAngle","°","Num","M","A2"]
[null,null,"喷雾夹角","SprayAngle","°","Num","R","A2"]
[null,null,"泡沫剂浓度","FoamingConcentrate","%","Num","R","A2"]
[null,null,"连接法兰类型","FlangeType",null,"Enum","R","D1","1. DN80 2. 151 3. 5418 4. 7819 5. DN100 99. 其他"]
[null,null,"最小用水连续供给时间","MinSupplyWaterTime","h","Num","M","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","R","L"]
[null,null,"工作电流","I","A","Inst","R","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","R","L"]
[null,null,"出口压力","OutPress","MPa","Inst","S","L"]
[null,null,"出水流量","OutFlow","m3/h","Inst","M","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计喷水量","AccSprayWater","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"出口压力设定","OutPressSet","MPa","Nump","S","L"]
["报警消息",null,"出口压力报警","OutPressAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"FSPS消防稳压设备","index":5,"n_rows":33,"n_cols":10,"rows_kept":33,"cut":false,"hidden":false,"merged":[[31,0,31,1],[32,0,32,1],[0,0,0,9],[1,0,1,1],[16,0,30,0],[2,0,15,1],[16,1,26,1],[27,1,30,1]]}
["消防稳压设备"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"故障报警与保护功能","AlarmFunc",null,"MEnum","M","D2","1. 过压 2. 欠压 3. 过流 4. 短路 5. 缺相 6. 水源缺水 99. 其他 (可多选）"]
[null,null,"消防工作额定压力","FireWaterRatedPress","MPa","Num","S","A2"]
[null,null,"消防储水标定容积","FireWaterStoreCap","m3","Num","S","A2"]
[null,null,"配用水泵额定流量","PumpRatedFlow","m3/h","Num","M","A2"]
[null,null,"配用水泵额定扬程","PumpRatedHead","m","Num","M","A2"]
[null,null,"配用水泵额定功率","PumpRatedP","kW","Num","M","A2"]
[null,null,"配用水泵额定转速","PumpRatedRPM","rpm","Num","M","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","M","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"消防工作压力","FireWaterPress","MPa","Inst","S","L"]
[null,null,"消防储水容量","FireWaterStore","m3","Inst","S","L"]
[null,null,"流量开关","FlowSwitch",null,"Boolv","S","L","0. 关闭 1. 开启"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数",null,"压力设定","PressSet","MPa","Nump","S","L"]
["报警消息",null,"压力报警","PressAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"FSFT泡沫储罐组","index":6,"n_rows":31,"n_cols":10,"rows_kept":31,"cut":false,"hidden":false,"merged":[[29,0,29,1],[30,0,30,1],[0,0,0,9],[1,0,1,1],[16,0,28,0],[2,0,15,1],[16,1,25,1],[26,1,28,1]]}
["泡沫储罐组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","R","A2"]
[null,null,"额定电压","RatedU","V","Num","R","A2"]
[null,null,"额定电流","RatedI","A","Num","R","A2"]
[null,null,"额定功率","RatedP","W","Num","R","A2"]
[null,null,"工作环境","WorkSite",null,"Enum","S","D1","1. 室内 2. 室外（有防晒、防雨、防冻装置） 99. 其他 "]
[null,null,"泡沫液类型","FoamingType",null,"Enum","M","D1","1. 环保型水成膜泡沫液 2. 蛋白、氟蛋白泡沫液 3. 抗溶性氟蛋白泡沫液 4. 抗溶性泡沫液 5. 耐温耐烟型高倍数泡沫液 99. 其他"]
[null,null,"泡沫液喷射时间","FoamingSprayTime","min","Num","R","A2",null," T= V/60*Q*λ\n(V表示泡沫罐容积（L），Q表示混合液流量（L/S）， λ表示混合比)"]
[null,null,"泡沫液储罐容量","FoamingStoreCap","m3","Num","S","A2"]
[null,null,"额定泡沫混合液流量","RatedFoamingMixFlow","m3/h","Num","M","A2"]
[null,null,"额定混合比","RatedMixRatio","%","Num","M","A2"]
[null,null,"最大压力损失","MaxPressLoss","MPa","Num","R","A2"]
[null,null,"混合装置出液管通径","OutPipeDiameter","mm","Num","R","A2"]
[null,null,"混合装置进水管通径","InPipeDiameter","mm","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"混合液储液量","FoamingMixStore","m3","Inst","M","L"]
[null,null,"混合比","MixRatio","%","Inst","R","M"]
[null,null,"泡沫混合液流量","FoamingMixFlow","m3/h","Inst","R","L"]
[null,null,"进液管压力","InPress","MPa","Inst","M","L"]
[null,null,"出液管压力","OutPress","MPa","Inst","M","L"]
[null,"累计指标","累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSAC消防空压机","index":7,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[38,0,38,1],[39,0,39,1],[0,0,0,9],[1,0,1,1],[22,0,37,0],[22,1,32,1],[33,1,37,1],[2,0,21,1]]}
["空压机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定压缩空气量","RatedCompressAir","kg/h","Num","S","A2"]
[null,null,"额定入口压力","RatedInPress","MPa","Num","R","A2"]
[null,null,"额定出口压力","RatedOutPress","MPa","Num","M","A2"]
[null,null,"储气罐容积","AirStoreCap","m3","Num","S","A2"]
[null,null,"最大转速","MaxRPM","rpm","Num","R","A2"]
[null,null,"最大离心力","MaxCentrifugalF","N","Num","R","A2"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"压缩空气流量","CompressAirFlow","kg/h","Inst","R","L"]
[null,null,"瞬时入口压力","InPress","MPa","Inst","R","L"]
[null,null,"瞬时出口压力","OutPress","MPa","Inst","M","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计压缩空气量","AccCompressAir","kg","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSWV湿式报警阀组","index":8,"n_rows":32,"n_cols":10,"rows_kept":32,"cut":false,"hidden":false,"merged":[[30,0,30,1],[31,0,31,1],[0,0,0,9],[1,0,1,1],[2,0,17,1],[18,0,29,0],[27,1,29,1],[18,1,26,1]]}
["湿式报警阀组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"额定电压","RatedU","V","Num","R","A2"]
[null,null,"监视电流","MonitorI","mA","Num","M","A2"]
[null,null,"报警电流","AlarmI","mA","Num","M","A2"]
[null,null,"额定出水流量","RatedOutWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定进水压力","RatedInWaterPress","MPa","Num","M","A2"]
[null,null,"额定出水压力","RatedOutWaterPress","MPa","Num","M","A2"]
[null,null,"球阀公称直径","BallValveDiameter","mm","Num","R","A2",null,"1.控制水力警铃报警管路水流；2.报警阀功能试验及系统检修时泄放存水"]
[null,null,"止回阀公称直径","CheckValveDiameter","mm","Num","R","A2",null,"单向补水，防止压力变化引起报警阀误动作"]
[null,null,"消防给水管公称直径","FireWaterPipeDN","mm","Num","R","A2"]
[null,null,"延迟器水容量","DelayerWaterCap","L","Num","R","A2",null,"防止水压变化引起误报"]
[null,null,"报警延迟时间","AlarmDelayTime","s","Num","M","A2"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"瞬时出口流量","OutWaterFlow","m3/h","Inst","R","L"]
[null,null,"瞬时进口压力","InWaterPress","MPa","Inst","M","L"]
[null,null,"瞬时出口压力","OutWaterPress","MPa","Inst","R","L"]
[null,null,"报警状态","AlarmStatus",null,"Boolv","S","L","0. 正常 1. 报警"]
[null,"累计指标","累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSDV干式报警阀组","index":9,"n_rows":35,"n_cols":10,"rows_kept":35,"cut":false,"hidden":false,"merged":[[33,0,33,1],[34,0,34,1],[0,0,0,9],[1,0,1,1],[2,0,20,1],[21,0,32,0],[21,1,29,1],[30,1,32,1]]}
["干式报警阀组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"额定电压","RatedU","V","Num","R","A2"]
[null,null,"监视电流","MonitorI","mA","Num","M","A2"]
[null,null,"报警电流","AlarmI","mA","Num","M","A2"]
[null,null,"额定排气量","RatedExhaustVolume","L","Num","M","A2"]
[null,null,"额定排气压力","RatedExhaustPress","Pa","Num","M","A2"]
[null,null,"额定排气时间","RatedExhaustTime","s","Num","S","A2"]
[null,null,"额定出水流量","RatedOutWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定进水压力","RatedInWaterPress","MPa","Num","M","A2"]
[null,null,"额定出水压力","RatedOutWaterPress","MPa","Num","M","A2"]
[null,null,"球阀公称直径","BallValveDiameter","mm","Num","R","A2",null,"1.控制水力警铃报警管路水流；2.报警阀功能试验及系统检修时泄放存水"]
[null,null,"止回阀公称直径","CheckValveDiameter","mm","Num","R","A2",null,"单向补水，防止压力变化引起报警阀误动作"]
[null,null,"消防给水管公称直径","FireWaterPipeDN","mm","Num","R","A2"]
[null,null,"延迟器水容量","DelayerWaterCap","L","Num","R","A2",null,"防止水压变化引起误报"]
[null,null,"报警延迟时间","AlarmDelayTime","s","Num","M","A2"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"瞬时出水流量","OutWaterFlow","m3/h","Inst","R","L"]
[null,null,"瞬时进口压力","InWaterPress","MPa","Inst","M","L"]
[null,null,"瞬时出口压力","OutWaterPress","MPa","Inst","R","L"]
[null,null,"报警状态","AlarmStatus",null,"Inst","S","L","0. 正常 1. 报警"]
[null,"累计指标","累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSPV预作用报警阀组","index":10,"n_rows":33,"n_cols":10,"rows_kept":33,"cut":false,"hidden":false,"merged":[[31,0,31,1],[32,0,32,1],[0,0,0,9],[1,0,1,1],[2,0,18,1],[19,0,30,0],[19,1,27,1],[28,1,30,1]]}
["预作用报警阀组"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"额定电压","RatedU","V","Num","R","A2"]
[null,null,"监视电流","MonitorI","mA","Num","M","A2"]
[null,null,"报警电流","AlarmI","mA","Num","M","A2"]
[null,null,"系统管网监控气压","MonitorPress","MPa","Num","S","A2"]
[null,null,"额定密封压力","RatedSealPress","MPa","Num","S","A2"]
[null,null,"额定出水流量","RatedOutWaterFlow","m3/h","Num","S","A2"]
[null,null,"额定进水压力","RatedInWaterPress","MPa","Num","M","A2"]
[null,null,"额定出水压力","RatedOutWaterPress","MPa","Num","M","A2"]
[null,null,"球阀公称直径","BallValveDiameter","mm","Num","R","A2",null,"1.控制水力警铃报警管路水流；2.报警阀功能试验及系统检修时泄放存水"]
[null,null,"止回阀公称直径","CheckValveDiameter","mm","Num","R","A2",null,"单向补水，防止压力变化引起报警阀误动作"]
[null,null,"消防给水管公称直径","FireWaterPipeDN","mm","Num","R","A2"]
[null,null,"报警延迟时间","AlarmDelayTime","s","Num","M","A2"]
[null,null,"防护等级","IPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"瞬时出水流量","OutWaterFlow","m3/h","Inst","R","L"]
[null,null,"瞬时进口压力","InWaterPress","MPa","Inst","M","L"]
[null,null,"瞬时出口压力","OutWaterPress","MPa","Inst","R","L"]
[null,null,"报警状态","AlarmStatus",null,"Boolv","S","L","0. 正常 1. 报警"]
[null,"累计指标","累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSHB消火栓箱","index":11,"n_rows":29,"n_cols":10,"rows_kept":29,"cut":false,"hidden":false,"merged":[[27,0,27,1],[28,0,28,1],[0,0,0,9],[1,0,1,1],[19,0,26,0],[24,1,26,1],[19,1,23,1],[2,0,18,1]]}
["消火栓箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"给水管公称直径","SupplyWaterPipeDiameter","mm","Num","R","A2"]
[null,null,"消火栓出口数量","FireHydrantOutNum","个","Num","M","A2"]
[null,null,"消防水带公称直径","FireHoseDN","mm","Num","R","A2"]
[null,null,"消防水带长度","FireHoseLength","m","Num","M","A2"]
[null,null,"消防水带数量","FireHoseNum","个","Num","M","A2"]
[null,null,"消防水枪喷嘴直径","FireHydrantGiantNozzleDiameter","mm","Num","R","A2"]
[null,null,"消防水枪数量","FireHydrantGiantNum","个","Num","M","A2"]
[null,null,"消防水枪出口压力","FireHydrantGiantRatedOutPress","MPa","Num","S","A2"]
[null,null,"消防水枪额定射程","FireHydrantGiantRatedRange","m","Num","S","A2"]
[null,null,"消防水枪出口流量","FireHydrantGiantRatedOutFlow","m3/h","Num","M","A2"]
[null,null,"控制按钮数量","CtrlButtonNum","个","Num","R","A2"]
[null,null,"指示灯数量","IndicateLightNum","个","Num","R","A2"]
[null,null,"接口额定强度压力","PortRatedStrengthPress","MPa","Num","R","A2"]
[null,null,"接口额定密封压力","PortRatedISealPress","MPa","Num","R","A2"]
[null,null,"接口额定工作压力","PortRatedWorkPress","MPa","Num","R","A2"]
[null,null,"是否带有手握式灭火器","isHandExtinguisher",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"阀门开度","ValveOpening","%","Inst","R","L"]
[null,null,"出水流量","OutWaterFlow","m3/h","Inst","R","L"]
[null,null,"出水压力","OutWaterPress","MPa","Inst","R","L"]
[null,"累计指标","累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSOH室外消火栓","index":12,"n_rows":19,"n_cols":10,"rows_kept":19,"cut":false,"hidden":false,"merged":[[17,0,17,1],[18,0,18,1],[0,0,0,9],[1,0,1,1],[9,0,16,0],[9,1,13,1],[14,1,16,1],[2,0,8,1]]}
["室外消火栓"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"管螺纹基本尺寸","PipeThreadSize","mm","Num","S","A2"]
[null,null,"螺纹公差","ThreadTolerance","mm","Num","R","A2"]
[null,null,"法兰尺寸","FlangeSize","mm","Num","R","A2"]
[null,null,"消防栓开启高度","FireHydrantLiftHeight","mm","Num","M","A2",null,"旋转阀杆从关闭状态到最大开启状态，将旋转圈数乘以阀杆的螺距，即为消火栓的开启高度"]
[null,null,"额定出口水压","RatedOutWaterPress","MPa","Num","S","A2"]
[null,null,"额定出口流量","RatedOutWaterFlow","m3/h","Num","S","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"阀门开度","ValveOpening","%","Inst","R","L"]
[null,null,"出水流量","OutWaterFlow","m3/h","Inst","R","L"]
[null,null,"出水压力","OutWaterPress","MPa","Inst","R","L"]
[null,"累计指标","累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSPC消防水泵接合器","index":13,"n_rows":13,"n_cols":10,"rows_kept":13,"cut":false,"hidden":false,"merged":[[12,0,12,1],[2,0,9,1],[0,0,0,9],[1,0,1,1],[10,0,10,1],[11,0,11,1]]}
["水泵接合器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"公称压力","RatedPress","MPa","Enum","S","A2"]
[null,null,"出口公称通径","OutDiameter","mm","Num","S","A2"]
[null,null,"法兰外径","FlangeOutDiameter","mm","Num","R","A2"]
[null,null,"螺栓孔直径","BoltHoleDiameter","mm","Num","R","A2"]
[null,null,"螺栓数","BoltNum","个","Num","R","A2"]
[null,null,"连接方式","ConnectType",null,"Enum","M","D1","1. 内螺纹 2. 外螺纹 3. 法兰 4. 焊接 5. 对焊 6. 承插焊 7. 卡套 8. 卡箍 99. 其他"]
[null,null,"驱动方式","DriveType",null,"Enum","R","D1","1. 手动 2. 气动 3. 液动 4. 电动 99. 其他"]
[null,null,"安装形式","InstallType",null,"Enum","R","D1","1. 地上式 2. 地下式 3. 墙壁式 4. 多用式 99. 其他"]
["运行参数",null,"是否外接水泵","isOutPump",null,"Boolv","M","E1","0. 否 1. 是"]
["设定参数"]
["报警消息"]

{"sheet":"FSTC消防伴热电缆","index":14,"n_rows":37,"n_cols":10,"rows_kept":37,"cut":false,"hidden":false,"merged":[[36,0,36,1],[1,0,1,1],[0,0,0,9],[20,0,34,0],[20,1,30,1],[31,1,34,1],[35,0,35,1],[2,0,19,1]]}
["伴热电缆"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"功率调节范围","PAdjustRange","kW","Num","R","A6"]
[null,null,"常温电阻","NormalTempResistance","Ω/m","Num","R","A2"]
[null,null,"电缆长度","CableLength","m","Num","R","A2"]
[null,null,"材质","MaterialType",null,"Enum","R","D1","1. 碳纤维 2. 玻璃纤维 3. 高分子PTC材料 99. 其他"]
[null,null,"弯曲半径","BendRadius","mm","Num","R","A2"]
[null,null,"导体截面半径","ConductorCrossRadius","mm","Num","R","A2"]
[null,null,"绝缘层厚度","InsulationThick","mm","Num","R","A2"]
[null,null,"最小绝缘电阻","MinInsulationResistance","Ω","Num","R","A2"]
[null,null,"最高暴露温度","MaxExposureTemp","℃","Num","M","A2",null,"电缆能承受的最高环境温度"]
[null,null,"最高维持温度","MaxHoldTemp","℃","Num","M","A2",null,"被伴热体系能维持的最高温度"]
[null,null,"最高表面温度","MaxSurfaceTemp","℃","Num","M","A2",null,"额定电压下伴热电缆表面能达到的最高温度"]
[null,null,"最大使用长度","MaxUseLength","m","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","R","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"阻燃等级","FlameRetardantLev",null,"Enum","M","D1","1. HB 2. V-2 3. V-1 4. V-0 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"暴露温度","ExposureTemp","℃","Inst","R","L"]
[null,null,"维持温度","HoldTemp","℃","Inst","R","L"]
[null,null,"表面温度","SurfaceTemp","℃","Inst","R","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSET消防末端试水装置","index":15,"n_rows":16,"n_cols":10,"rows_kept":16,"cut":false,"hidden":false,"merged":[[15,0,15,1],[0,0,0,9],[1,0,1,1],[12,0,13,1],[2,0,11,1],[14,0,14,1]]}
["末端试水装置"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电磁阀电压","SolenoidValveU","V","Num","R","A2"]
[null,null,"电磁阀电流","SolenoidValveI","mA","Num","R","A2"]
[null,null,"进口螺纹尺寸","InThreadSize","mm","Num","R","A2"]
[null,null,"出口螺纹尺寸","OutThreadSize","mm","Num","R","A2"]
[null,null,"公称直径","DN","mm","Num","S","A2"]
[null,null,"密封试验压力","SealTestPress","MPa","Num","R","A2"]
[null,null,"流量特性曲线系数","Cv",null,"Num","R","A1"]
[null,null,"压力表精度","PressMeterPresicion","MPa","Num","M","A2"]
[null,null,"压力表量程","PressMeterRange","MPa","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
["运行参数",null,"阀门开度","ValveOpening","%","Inst","S","L"]
[null,null,"压力表读数","Press","MPa","Inst","M","L"]
["设定参数"]
["报警消息"]

{"sheet":"FSWT消防水箱","index":16,"n_rows":40,"n_cols":10,"rows_kept":40,"cut":false,"hidden":false,"merged":[[37,0,37,1],[38,0,39,1],[26,0,36,1],[1,0,1,1],[0,0,0,9],[2,0,25,0],[2,1,19,1],[20,1,22,1],[23,1,25,1]]}
["水箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","内胆","水箱长度","TankLength","m","Num","R","A2"]
[null,null,"水箱宽度","TankWidth","m","Num","R","A2"]
[null,null,"水箱高度","TankHeight","m","Num","R","A2"]
[null,null,"水箱容积","TankCap","m3","Num","S","A2"]
[null,null,"内胆材质","LiningMaterial",null,"Enum","R","D1","1. 不锈钢 2. 搪瓷 3. 塑料 4. 复合材料 99. 其他"]
[null,null,"最大承压","MaxPress","MPa","Num","M","A2"]
[null,null,"底板厚度","BottomBoardThick","mm","Num","R","A2"]
[null,null,"侧板厚度","SideBoardThick","mm","Num","R","A2"]
[null,null,"顶板厚度","TopBoardThick","mm","Num","R","A2"]
[null,null,"进水口截面积","InCrossArea","m2","Num","R","A2"]
[null,null,"出水口截面积","OutCrossArea","m2","Num","R","A2"]
[null,null,"溢流口截面积","OverflowCrossArea","m2","Num","R","A2"]
[null,null,"排污口截面积","SewageCrossArea","m2","Num","R","A2"]
[null,null,"人孔宽度","ManholeWidth","m","Num","R","A2"]
[null,null,"人孔高度","ManholeHeight","m","Num","R","A2"]
[null,null,"内外爬梯高度","LadderHeight","m","Num","R","A2"]
[null,null,"额定水温","RatedWaterTemp","℃","Num","R","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,"保温层","是否有保温层","isInsulation",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"保温层材料","InsulationMaterial",null,"Enum","R","D1","1. 岩棉 2. 玻璃棉 3. 聚氨酯 4. 聚苯乙烯 5. 酚醛泡沫 99. 其他"]
[null,null,"保温层厚度","InsulationThick","mm","Num","R","A2"]
[null,"外壳","是否有外壳","isShield",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"外壳材质","ShieldMaterial ",null,"Enum","R","D1","1. 不锈钢 2. 塑料 99. 其他"]
[null,null,"外壳抗压强度","ShieldCompressiveStrength","MPa","Num","R","A2"]
["运行参数",null,"水箱水位","TankWaterLev","m","Inst","S","L"]
[null,null,"水箱水量","TankWaterVolume","m3","Inst","R","L"]
[null,null,"水箱水温","TankWaterTemp","℃","Inst","M","L"]
[null,null,"进水流量","WaterInFlow","m3/h","Inst","R","L"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"溢流流量","OverflowFlow","m3/h","Inst","R","L"]
[null,null,"排污流量","SewageFlow","m3/h","Inst","R","L"]
[null,null,"进水温度","WaterInTemp","℃","Inst","R","L"]
[null,null,"进水口压力","WaterInPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"出水口压力","WaterOutPress","MPa","Inst","R","L"]
["设定参数"]
["报警消息",null,"高液位报警","HighLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]
[null,null,"低液位报警","LowLevAlarm",null,"Boolp","S","L","0. 正常 1. 报警"]

{"sheet":"FSFP消防补水泵","index":17,"n_rows":77,"n_cols":10,"rows_kept":77,"cut":false,"hidden":false,"merged":[[73,0,75,1],[76,0,76,1],[67,1,72,1],[1,0,1,1],[0,0,0,9],[2,0,40,0],[37,1,40,1],[41,0,72,0],[41,1,61,1],[62,1,66,1],[2,1,36,1]]}
["水泵"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq ","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"额定频率","RatedFreq","Hz","Num","S","A2"]
[null,null,"水泵类型","PumpType",null,"Enum","R","D1","1. 容积式 1.1 往复式活塞泵 1.2 往复式柱塞泵 1.3 往复式隔膜泵 1.4 回转式齿轮泵 1.5 回转式螺杆泵 1.6 回转式叶片泵 2. 叶轮式 2.1 离心泵 2.2 轴流泵 2.3 混流泵 2.4 旋涡泵 3. 射流泵 99. 其他"]
[null,null,"泵体安装类型","InstallType",null,"Enum","R","D1","1. 立式 2. 卧式 99. 其他"]
[null,null,"输配介质","MediumType",null,"Enum","M","D1","1. 水 2. 乙二醇 3. 海水 4. 无机盐溶液 5. 泡沫液 99. 其他"]
[null,null,"调节类型","AdjustType",null,"Enum","M","D1","1. 定频无调节 2. 二档调节 3. 三档调节 4. 变频调节 99. 其他"]
[null,null,"管网使用类型","NetUseType",null,"Enum","M","D1","1. 一次泵 2. 二次泵 3. 补水泵 4. 加压泵 99. 其他"]
[null,null,"是否为备用泵","isBackup",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"额定扬程","RatedHead","m","Num","S","A2"]
[null,null,"额定驱动压力","RatedDrivePress","MPa","Num","R","A2"]
[null,null,"额定增压比","RatedPressRatio",null,"Num","R","A1"]
[null,null,"额定流量","RatedFlow","m3/h","Num","S","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","S","A2"]
[null,null,"是否有变频功能","isVFD",null,"Bool","S","E1","0. 定频 1. 变频"]
[null,null,"是否有档位选项","isGear",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水泵直径","PumpDiameter","mm","Num","R","A2",null,"口径"]
[null,null,"电机额定效率","RatedMotorEff","%","Num","R","A2"]
[null,null,"水泵额定效率","RatedPumpEff","%","Num","M","A2"]
[null,null,"特性曲线","CharacterCurve",null,"Attachment","R","F1"]
[null,null,"是否有减压型倒流防止器","isBackflowPreventer    ",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"适用场所","ApplySite",null,"Enum","R","D1","1. 室内 2. 室外 99. 其他"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"振动烈度","Vibration","mm/s","Num","M","A2"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
[null,"辅助设备","变频器型号","VFDSpecification",null,"Str","R","B1"]
[null,null,"变频最高频率","VFDMaxFreq ","Hz","Num","M","A2"]
[null,null,"变频最低频率","VFDMinFreq ","Hz","Num","M","A2"]
[null,null,"过滤器型号","FilterSpecification",null,"Str","R","B1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"A相电压","APhaseU","V","Inst","M","L"]
[null,null,"B相电压","BPhaseU","V","Inst","M","L"]
[null,null,"C相电压","CPhaseU","V","Inst","M","L"]
[null,null,"A相电流","APhaseI","A","Inst","M","L"]
[null,null,"B相电流","BPhaseI","A","Inst","M","L"]
[null,null,"C相电流","CPhaseI","A","Inst","M","L"]
[null,null,"平均电压","U","V","Inst","M","L"]
[null,null,"平均电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L",null,"三相有功功率"]
[null,null,"运行频率","WorkFreq","Hz","Inst","S","L"]
[null,null,"工作档位","Gear",null,"Enumv","S","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"瞬时流量","Flow","m3/h","Inst","M","L"]
[null,null,"水泵进口压力","InPress","MPa","Inst","M","L"]
[null,null,"水泵出口压力","OutPress","MPa","Inst","M","L"]
[null,null,"过滤器进口压力","FilterInPress","MPa","Inst","R","L"]
[null,null,"过滤器出口压力","FilterOutPress","MPa","Inst","R","L"]
[null,"瞬时指标","水泵扬程","Head","m","Inst","M","M"]
[null,null,"瞬时增压比","PressRatio",null,"Inst","M","M"]
[null,null,"电机效率","MotorEff","%","Inst","R","M"]
[null,null,"水泵效率","PumpEff","%","Inst","R","M"]
[null,null,"整体效率","OverallEff","%","Inst","R","M"]
[null,"累计指标","累计流量","AccFlow","m3","Acc","R","M"]
[null,null,"累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
[null,null,"日补水量","DayFilling","m3","Acc","M","M",null,"补水泵"]
["设定参数",null,"设备开关设定","EquipSwitchSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
[null,null,"设备频率设定","EquipFreqSet","Hz","Nump","S"]
[null,null,"设备档位设定","EquipGearSet",null,"Enump","S",null,"1. 低档 2. 中档 3. 高档 99. 其他"]
["报警消息"]

{"sheet":"FSSN消防喷头","index":18,"n_rows":30,"n_cols":10,"rows_kept":30,"cut":false,"hidden":false,"merged":[[0,0,0,9],[28,0,28,1],[29,0,29,1],[1,0,1,1],[2,0,12,1],[13,0,27,0],[13,1,23,1],[24,1,27,1]]}
["喷头"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"功能类型","FuncType",null,"Enum","S","D1","1. 喷灌喷头 2. 水景喷头 99. 其他"]
[null,null,"喷头类型","NozzleType",null,"Enum","M","D1","1. 庭院喷头 2. 地埋式喷头 3. 摇臂式喷头 99. 其他","喷灌喷头"]
[null,null,"喷洒方式","SprayType",null,"Enum","R","D1","1. 散射 2. 射线 3. 旋转 4. 射线旋转 99. 其他","喷灌喷头"]
[null,null,"喷射形状","ShapeType",null,"Enum","R","D1","1. 万向直流 2. 旋转 3. 凤尾 4. 集束 5. 礼花 6. 半球 7. 环形 8. 扇形 9. 蒲公英 10. 半蒲公英 11. 玉柱 12. 雪松 13. 涌泉 14. 水雾 99. 其它","水景喷头"]
[null,null,"喷嘴直径","NozzleDiameter","mm","Num","M","A2"]
[null,null,"额定出水量","RatedWaterOutFlow","m3/h","Num","M","A2"]
[null,null,"额定出水流速","RatedWaterOutV","m/s","Num","M","A2"]
[null,null,"额定射程","RatedSprayRange","m","Num","R","A2"]
[null,null,"理论压损","RatedPressLoss","MPa","Num","R","A2"]
[null,null,"喷洒扇形角度","MaxSprayAngle","°","Num","R","A2"]
[null,null,"喷嘴材质","NozzleMaterial",null,"Enum","R","D1","1. 黄铜 2. 不锈钢 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"出水流量","WaterOutFlow","m3/h","Inst","R","L"]
[null,null,"出口流速","WaterOutV","m/s","Inst","R","L"]
[null,null,"出水压力","WaterOutPress","MPa","Inst","R","L"]
[null,null,"出水温度","WaterOutTemp","℃","Inst","R","L"]
[null,null,"射程","SprayRange","m","Inst","R","M"]
[null,null,"阀门开度","ValveOpening","%","Inst","M","L"]
[null,"累计指标","累计出水量","AccSprayVolume","m3","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime","h","Acc","R","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"FSCP消火栓控制面板","index":19,"n_rows":20,"n_cols":10,"rows_kept":20,"cut":false,"hidden":false,"merged":[[19,0,19,1],[0,0,0,9],[1,0,1,1],[2,0,14,1],[15,0,17,1],[18,0,18,1]]}
["控制面板"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"通信方式","CommunicationType",null,"Enum","S","D1","1. RS485 2. CAN 3. TTL 4. RS232 99. 其他"]
[null,null,"安装方式","InstallType",null,"Enum","M","D1","1. 嵌入式安装 2. 标准86型底盒 3. 支架安装 99.其他"]
[null,null,"输入方式","InputType",null,"MEnum","S","D2","1. 按键输入 2. 触屏输入 3. 旋钮输入 99. 其他 （可多选）"]
[null,null,"触屏尺寸","TouchScreenSize","寸","Num","R","A2"]
[null,null,"是否具有USB下载接口","isUSB?",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"回路数","LoopNum","路","Num","R","A2"]
[null,null,"接口开关量个数","ValueNum","个","Num","R","A2"]
[null,null,"是否具有无线功能","isWifi",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"无线距离","WifiDist","m","Num","M","A2"]
[null,null,"无线频率","WifiFreq","MHz","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange ","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange ","%RH","Numr","M","A6"]
["运行参数",null,"开关状态","OnOffStatus",null,"Boolv","M","L","0. 关 1. 开"]
[null,null,"档位状态","GearStatus",null,"Enumv","M","L","1. 低档 2. 中档 3. 高档 99. 其他"]
[null,null,"设定值状态","SetValueStatus",null,"Inst","M","L"]
["设定参数"]
["报警消息"]

{"sheet":"FSCU消防给水控制箱","index":20,"n_rows":61,"n_cols":10,"rows_kept":61,"cut":false,"hidden":false,"merged":[[60,0,60,1],[1,0,1,1],[18,1,48,1],[49,1,53,1],[0,0,0,9],[2,0,48,0],[49,0,58,0],[54,1,58,1],[59,0,59,1],[2,1,17,1]]}
["控制箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","额定输入电压","RatedInputU","V","Num","R","A2"]
[null,null,"额定输出电压","RatedOutputU","V","Num","R","A2"]
[null,null,"应答时间","ResponseTime","ms","Num","M","A2"]
[null,null,"允许瞬时断电时间","AllowPowerOffTime ","ms","Num","M","A2"]
[null,null,"是否有网络功能","isNetwork",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"IP地址","IPAddress",null,"Str","S","B1"]
[null,null,"子网掩码","SubnetMask",null,"Str","S","B1"]
[null,null,"网关","Gateway",null,"Str","S","B1"]
[null,null,"DNS服务器地址","DNS",null,"Str","S","B1"]
[null,null,"适用网络类型","NetType",null,"Enum","M","D1","1. 千兆以太网 2. 万兆以太网 3. 光纤 99. 其他"]
[null,null,"传输速率","TransferSpeed","MB/s","Num","M","A2"]
[null,null,"主芯片类型","MainChip",null,"Str","R","B1"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange ","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,"接口","输入485接口数量","In485PortNum","个","Num","R","A2"]
[null,null,"输出485接口数量","Out485PortNum","个","Num","R","A2"]
[null,null,"输入232接口数量","In232PortNum","个","Num","R","A2"]
[null,null,"输出232接口数量","Out232PortNum","个","Num","R","A2"]
[null,null,"输入422接口数量","In422PortNum","个","Num","R","A2"]
[null,null,"输出422接口数量","Out422PortNum","个","Num","R","A2"]
[null,null,"输入MBUS接口数量","InMBUSPortNum","个","Num","R","A2"]
[null,null,"输出MBUS接口数量","OutMBUSPortNum","个","Num","R","A2"]
[null,null,"输入音频接口数量","InAudioPortNum","个","Num","R","A2"]
[null,null,"输出音频接口数量","OutAudioPortNum","个","Num","R","A2"]
[null,null,"HDMI接口数量","HDMIPortNum","个","Num","R","A2"]
[null,null,"VGA接口数量","VGAPortNum","个","Num","R","A2"]
[null,null,"USB接口数量","USBPortNum","个","Num","R","A2"]
[null,null,"以太网接口数量","EthernetPortNum ","个","Num","R","A2"]
[null,null,"光纤接口数量","FiberPortNum ","个","Num","R","A2"]
[null,null,"电压AI接口数量","AIUPortNum","个","Num","R","A2"]
[null,null,"电压AI信号","AIU","V","Num","R","A2"]
[null,null,"电流AI接口数量","AIIPortNum","个","Num","R","A2"]
[null,null,"电流AI信号","AII","A","Num","R","A2"]
[null,null,"电压AO接口数量","AOUPortNum","个","Num","R","A2"]
[null,null,"电压AO信号","AOU","V","Num","R","A2"]
[null,null,"电流AO接口数量","AOIPortNum","个","Num","R","A2"]
[null,null,"电流AO信号","AOI","A","Num","R","A2"]
[null,null,"DI干节点接口数量","DIDryNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点接口数量","DIWetNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点电压","DIWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"DO干节点接口数量","DODryNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点接口数量","DOWetNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点电压","DOWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"输入同轴线接口数量","InCoaxialPortNum","个","Num","R","A2"]
[null,null,"输出同轴线接口数量","OutCoaxialPortNum","个","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"在线状态","OnlineStatus",null,"Boolv","S","L","0. 脱线 1. 在线"]
[null,null,"上传速度","UploadSpeed","MB/s","Inst","R","L"]
[null,null,"下载速度","DownloadSpeed","MB/s","Inst","R","L"]
[null,"累计指标","累计上传数据量","AccUploadData","GB","Acc","R","L"]
[null,null,"累计下载数据量","AccDownloadData","GB","Acc","R","L"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","L"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","L"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]