{"text_format":"2","workbook":"xlsx","n_sheets":4,"sheets":["ELEL直梯","ELES扶梯","ELCU电梯控制箱","ELET电梯曳引机"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"ELEL直梯","index":0,"n_rows":56,"n_cols":10,"rows_kept":56,"cut":false,"hidden":false,"merged":[[54,0,55,1],[53,0,53,1],[0,0,0,9],[1,0,1,1],[34,0,52,0],[34,1,47,1],[48,1,52,1],[2,0,33,1]]}
["直梯"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"用途类型","FuncType",null,"Enum","S","D1","1. 客梯 2. 货梯 99. 其他"]
[null,null,"是否是观光电梯","isSight",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"最大载荷","MaxLoad","kg","Num","S","A2"]
[null,null,"最大载客数","MaxPassengerNum","人","Num","S","A2"]
[null,null,"额定速度","RatedV","m/s","Num","R","A2"]
[null,null,"电梯内长度","InLength","mm","Num","R","A2"]
[null,null,"电梯内宽度","InWidth","mm","Num","R","A2"]
[null,null,"电梯内高度","InHeight","mm","Num","R","A2"]
[null,null,"门宽","DoorWidth ","mm","Num","R","A2"]
[null,null,"井道长度","WellLength","mm","Num","R","A2"]
[null,null,"井道宽度","WellWidth","mm","Num","R","A2"]
[null,null,"底坑深度","PitDepth","mm","Num","R","A2"]
[null,null,"驱动方式","DriveType",null,"Enum","R","D1","1. 直流驱动 2. 交流单速驱动 3. 交流双速驱动 4. 交流调压驱动 5. 交流变压变频驱动 6. 永磁同步电机驱动 7. 液压驱动 99. 其他"]
[null,null,"操纵控制方式","CtrlType",null,"Enum","R","D1","1. 手柄开关控制 2. 按钮控制 3. 信号控制 4. 集选控制 5. 并联控制 6. 群控 99. 其他"]
[null,null,"厅轿门形式","DoorType",null,"Enum","R","D1","1. 中分式 2. 旁开式 3. 直分式 99. 其他"]
[null,null,"左右开门方向","OpenDirectType",null,"Bool","R","E1","0. 左开门 1. 右开门"]
[null,null,"机房形式","MachineRoomType",null,"Enum","M","D1","1. 上机房 2. 下机房 3. 无机房 99. 其他"]
[null,null,"层站数","StopNum","站","Num","S","A2",null,"电梯运行其中的建筑的层楼称为层，各层楼用以进出轿厢的地点称为站。"]
[null,null,"抗震能力","SeismicCapacity",null,"Enum","S","D1","参考《10抗震设防烈度》"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange ","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"当前载荷","Load","kg","Inst","M","L"]
[null,null,"当前乘客数","PassengerNum","人","Inst","R","L"]
[null,null,"运行方向","MoveDirect",null,"Enumv","S","L","1. 向上 2. 向下 3. 静止 99. 其他"]
[null,null,"当前层数","StopFloor","层","Inst","S","L"]
[null,null,"需停站个数","NeedStopNum","个","Inst","R","L"]
[null,null,"需停站位置","NeedStopFloor",null,"Inst","R","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运送人次","AccPassengerNum","人次","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime ","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息",null,"A1级故障","A1LevAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]
[null,null,"A2级故障","A2LevAlarm",null,"Boolp","S","L","0. 正常 1. 故障"]

{"sheet":"ELES扶梯","index":1,"n_rows":47,"n_cols":10,"rows_kept":47,"cut":false,"hidden":false,"merged":[[45,0,45,1],[46,0,46,1],[28,1,39,1],[40,1,44,1],[0,0,0,9],[1,0,1,1],[28,0,44,0],[2,0,27,1]]}
["扶梯"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"功能类型","FuncType",null,"Enum","S","D1","1. 自动扶梯 2. 自动人行道 99. 其他"]
[null,null,"最大载荷","MaxLoad","kg","Num","S","A2"]
[null,null,"理论输送能力","RatedDeliveryCap","人次/5min","Num","M","A2"]
[null,null,"是否有感应调速功能","isSensorSpeedCtrl",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"无载荷时速度","RatedNonLoadV","m/s","Num","R","A2"]
[null,null,"有载荷时速度","RatedLoadV","m/s","Num","R","A2"]
[null,null,"倾斜角","SlantAngle","°","Num","R","A2"]
[null,null,"高度","EscalatorHeight","mm","Num","R","A2"]
[null,null,"长度","EscalatorLength","mm","Num","R","A2"]
[null,null,"宽度","EscalatorWidth","mm","Num","R","A2"]
[null,null,"梯级宽度","StepWidth","mm","Num","R","A2"]
[null,null,"基坑深度","PitDepth","mm","Num","R","A2",null,"自动扶梯空载和负载向下制动距离范围"]
[null,null,"抗震能力","SeismicCapacity",null,"Enum","S","D1","参考《10抗震设防烈度》"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange ","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"当前载荷","Load","kg","Inst","M","L"]
[null,null,"当前输送人流量","DeliveryFlow","人次/5min","Inst","R","L"]
[null,null,"运行方向","MoveDirect",null,"Enumv","S","L","1. 向上 2. 向下 3. 静止 99. 其他"]
[null,null,"运行速度","MoveV","m/s","Inst","R","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运送人次","AccPassengerNum","人次","Acc","R","M"]
[null,null,"累计运行时间","AccRunTime ","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ELCU电梯控制箱","index":2,"n_rows":61,"n_cols":10,"rows_kept":61,"cut":false,"hidden":false,"merged":[[0,0,0,9],[2,0,48,0],[60,0,60,1],[59,0,59,1],[1,0,1,1],[18,1,48,1],[49,0,58,0],[49,1,53,1],[54,1,58,1],[2,1,17,1]]}
["控制箱"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","额定输入电压","RatedInputU","V","Num","R","A2"]
[null,null,"额定输出电压","RatedOutputU","V","Num","R","A2"]
[null,null,"应答时间","ResponseTime","ms","Num","M","A2"]
[null,null,"允许瞬时断电时间","AllowPowerOffTime ","ms","Num","M","A2"]
[null,null,"是否有网络功能","isNetwork",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"IP地址","IPAddress",null,"Str","S","B1"]
[null,null,"子网掩码","SubnetMask",null,"Str","S","B1"]
[null,null,"网关","Gateway",null,"Str","S","B1"]
[null,null,"DNS服务器地址","DNS",null,"Str","S","B1"]
[null,null,"适用网络类型","NetType",null,"Enum","M","D1","1. 千兆以太网 2. 万兆以太网 3. 光纤 99. 其他"]
[null,null,"传输速率","TransferSpeed","MB/s","Num","M","A2"]
[null,null,"主芯片类型","MainChip",null,"Str","R","B1"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange ","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,"接口","输入485接口数量","In485PortNum","个","Num","R","A2"]
[null,null,"输出485接口数量","Out485PortNum","个","Num","R","A2"]
[null,null,"输入232接口数量","In232PortNum","个","Num","R","A2"]
[null,null,"输出232接口数量","Out232PortNum","个","Num","R","A2"]
[null,null,"输入422接口数量","In422PortNum","个","Num","R","A2"]
[null,null,"输出422接口数量","Out422PortNum","个","Num","R","A2"]
[null,null,"输入MBUS接口数量","InMBUSPortNum","个","Num","R","A2"]
[null,null,"输出MBUS接口数量","OutMBUSPortNum","个","Num","R","A2"]
[null,null,"输入音频接口数量","InAudioPortNum","个","Num","R","A2"]
[null,null,"输出音频接口数量","OutAudioPortNum","个","Num","R","A2"]
[null,null,"HDMI接口数量","HDMIPortNum","个","Num","R","A2"]
[null,null,"VGA接口数量","VGAPortNum","个","Num","R","A2"]
[null,null,"USB接口数量","USBPortNum","个","Num","R","A2"]
[null,null,"以太网接口数量","EthernetPortNum ","个","Num","R","A2"]
[null,null,"光纤接口数量","FiberPortNum ","个","Num","R","A2"]
[null,null,"电压AI接口数量","AIUPortNum","个","Num","R","A2"]
[null,null,"电压AI信号","AIU","V","Num","R","A2"]
[null,null,"电流AI接口数量","AIIPortNum","个","Num","R","A2"]
[null,null,"电流AI信号","AII","A","Num","R","A2"]
[null,null,"电压AO接口数量","AOUPortNum","个","Num","R","A2"]
[null,null,"电压AO信号","AOU","V","Num","R","A2"]
[null,null,"电流AO接口数量","AOIPortNum","个","Num","R","A2"]
[null,null,"电流AO信号","AOI","A","Num","R","A2"]
[null,null,"DI干节点接口数量","DIDryNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点接口数量","DIWetNodePortNum","个","Num","R","A2"]
[null,null,"DI湿节点电压","DIWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"DO干节点接口数量","DODryNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点接口数量","DOWetNodePortNum","个","Num","R","A2"]
[null,null,"DO湿节点电压","DOWetNodeU",null,"Enum","R","D1","1. DC0～30V（标准DC24V） 2. AC110～220V 99. 其他"]
[null,null,"输入同轴线接口数量","InCoaxialPortNum","个","Num","R","A2"]
[null,null,"输出同轴线接口数量","OutCoaxialPortNum","个","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"在线状态","OnlineStatus",null,"Boolv","S","L","0. 脱线 1. 在线"]
[null,null,"上传速度","UploadSpeed","MB/s","Inst","R","L"]
[null,null,"下载速度","DownloadSpeed","MB/s","Inst","R","L"]
[null,"累计指标","累计上传数据量","AccUploadData","GB","Acc","R","L"]
[null,null,"累计下载数据量","AccDownloadData","GB","Acc","R","L"]
[null,null,"累计运行时间","AccRunTime","h","Acc","M","L"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","L"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"ELET电梯曳引机","index":3,"n_rows":68,"n_cols":10,"rows_kept":68,"cut":false,"hidden":false,"merged":[[49,0,65,0],[62,1,65,1],[0,0,0,9],[66,0,66,1],[67,0,67,1],[49,1,61,1],[1,0,1,1],[2,0,48,0],[2,1,27,1],[28,1,33,1],[34,1,40,1],[41,1,46,1],[47,1,48,1]]}
["电梯曳引机"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整机","电源频率","PowerFreq","Hz","Num","M","A2"]
[null,null,"额定电压","RatedU","V","Num","S","A2"]
[null,null,"额定电流","RatedI","A","Num","M","A2"]
[null,null,"额定功率","RatedP","kW","Num","S","A2"]
[null,null,"是否有齿轮","isGear",null,"Bool","M","E1","0. 有齿轮牵引机 1. 无齿轮牵引机"]
[null,null,"电梯用途分类","ElevatorType",null,"Enum","S","D1","1. 乘客电梯 2. 载货电梯 3. 客货电梯 4. 住宅电梯 5. 杂物电梯 6. 船用电梯 7. 汽车用电梯 8. 观光电梯 9. 病床电梯 99. 其他"]
[null,null,"额定速度","RatedV","m/s","Num","M","A2",null,"牵引轮节圆直径上的线速度"]
[null,null,"额定转矩","RatedTorque","Nm","Num","M","A2",null,"额定电压和额定频率时，牵引机输出的转矩"]
[null,null,"许用径向载荷","AllowRadialLoad","kg","Num","R","A2",null,"牵引轮上允许承受的最大径向载荷"]
[null,null,"最大轴负荷","MaxAxleLoad","kg","Num","R","A2"]
[null,null,"额定启（制）动次数","RatedHourStartCount","次/h","Num","R","A2",null,"允许的每小时启（制）动次数"]
[null,null,"曳引比","TractionRatio",null,"Num","R","A1",null,"牵引轮的圆周速度与轿厢速度之比"]
[null,null,"电流过载能力","OverICapacity","A","Num","R","A2"]
[null,null,"额定载重量","RatedLoad","kg","Num","S","A2",null,"电梯设计所规定的轿厢内最大载荷"]
[null,null,"额定提升高度","RatedLiftHeight","m","Num","S","A2"]
[null,null,"绳槽节距","SlotPitch","mm","Num","R","A2"]
[null,null,"曳引轮直径","PulleyD","mm","Num","R","A2"]
[null,null,"抗震能力","SeismicCapacity",null,"Enum","S","D1","参考《10抗震设防烈度》"]
[null,null,"电机防护等级","MotorIPGrade",null,"Str","M","B1","参考《11防护等级》"]
[null,null,"电机绝缘等级","MotorInsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"工作温度范围","WorkTempRange ","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"噪声强度","Noise","dB(A)","Num","M","A2"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,"电动机","电动机类型","MotorType",null,"Enum","M","D1","1.直流电动机 2.交流同步电动机 3.交流异步电动机 99. 其他"]
[null,null,"堵转电流","LockedRotorI","A","Num","R","A2"]
[null,null,"堵转转矩","LockedRotorTorque","Nm","Num","R","A2",null,"在电机额定电压下启动时，当在转轴上加至其一转矩时，电机将无法启动，这个就是堵转转矩"]
[null,null,"额定功率因数","RatedPowerFactor",null,"Num","R","A2"]
[null,null,"额定转速","RatedRPM","rpm","Num","R","A2"]
[null,null,"定子极对数","PoleNumber","对","Num","R","A2"]
[null,"制动器","制动器类型","BrakeType",null,"Enum","M","D1","1. 翼式制动器 2. 块式制动器 3. 盘式制动器 4. 钳式制动器 99. 其他"]
[null,null,"开启滞后时间","LagT","ms","Num","R","A2",null,"制动器断电到制动力矩达到额定值的时间"]
[null,null,"制动半径","BrakeRadius","mm","Num","R","A2",null,"转动中心到摩擦片受力中心的距离 "]
[null,null,"制动力矩","BrakeTorque","Nm","Num","R","A2",null,"制动力矩是由制动器产生的力矩"]
[null,null,"电磁线圈供电方式","CoilPowerType",null,"Enum","R","D1","1. 交流供电 2. 直流供电 99. 其他"]
[null,null,"最低起动电压","MinStartV","V","Num","R","A2"]
[null,null,"最高释放电压","MaxReleaseV","V","Num","R","A2"]
[null,"减速器","是否具有减速器","isReducer",null,"Bool","M","E1","0. 否 1. 是","有齿牵引机有减速器；无齿牵引机无减速器"]
[null,null,"减速箱传动方式","ReducerDriveType",null,"Enum","M","D1","1. 涡轮蜗杆传动 2. 斜齿轮传动 99. 其他"]
[null,null,"减速比","ReduceRatio",null,"Num","R","A1",null,"曳引机输入轴的转速和输出轴的转速比例"]
[null,null,"输出轴转速","OutAxleRPM","rpm","Num","R","A2"]
[null,null,"润滑方式","LubricationType",null,"Enum","R","D1","1. 脂润滑 2. 浸油润滑 3. 喷油润滑 99. 其他"]
[null,null,"蜗轮蜗杆轴向间隙","TurbineWormGap","mm","Num","R","A2",null,"有齿轮牵引机才有涡轮蜗杆，涡轮蜗杆位于采用涡轮蜗杆传动的减速箱"]
[null,"联轴器","联轴器类型","CouplerType",null,"Enum","M","D1","1. 刚性联轴器 2. 无弹性元件挠性联轴器 3. 有弹性元件挠性联轴器 99. 其他"]
[null,null,"联轴器公称转矩","CouplerRatedTorque","Nm","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"工作电压","U","V","Inst","M","L"]
[null,null,"工作电流","I","A","Inst","M","L"]
[null,null,"耗电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"当前载重量","Load","kg","Inst","M","L"]
[null,null,"运行速度","MoveV","m/s","Inst","M","L"]
[null,null,"电机温升","MotorTempRise","℃","Inst","R","L"]
[null,null,"润滑油油温升","LubricantTempRise","℃","Inst","R","L"]
[null,null,"一小时电动机起动次数","HourStartCount","次/h","Inst","R","M"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计运行时间","AccRunTime ","h","Acc","S","M"]
[null,null,"开启时间计时","OpenTimeCount","h","Acc","R","M"]
[null,null,"关闭时间计时","CloseTimeCount","h","Acc","R","M"]
["设定参数"]
["报警消息"]