{"text_format":"2","workbook":"xlsx","n_sheets":13,"sheets":["List","通用分区","供电分区","照明分区","网络分区","空调分区","采暖分区","洁净分区","生活给水分区","防火分区","安防分区","租户分区","功能分区"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"List","index":0,"n_rows":14,"n_cols":5,"rows_kept":14,"cut":false,"hidden":false,"merged":[]}
[]
[null,"序号","业务空间类别","英文编码","英文全称"]
[null,0,"通用分区","CMZ","GeneralZone"]
[null,1,"供电分区","PSZ","PowerSupplyZone"]
[null,2,"照明分区","LTZ","LightingZone"]
[null,3,"网络分区","NWZ","NetworkZone"]
[null,4,"空调分区","ACZ","AirConditioningZone"]
[null,5,"采暖分区","HTZ","HeatingZone"]
[null,6,"洁净分区","CLZ","CleanZone"]
[null,7,"生活给水分区","DWZ","DomesticWaterSupplyZone"]
[null,8,"防火分区","FRZ","FireZone"]
[null,9,"安防分区","SCZ","SecurityZone"]
[null,10,"租户分区","TNZ","TenantZone"]
[null,11,"功能分区","FCZ","FunctionZone"]

{"sheet":"通用分区","index":1,"n_rows":74,"n_cols":10,"rows_kept":74,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,2,1],[3,0,3,1],[73,0,73,1],[4,0,17,1],[45,0,48,1],[49,0,71,0],[49,1,63,1],[64,1,71,1],[72,0,72,1],[18,0,19,1],[20,0,44,0],[20,1,27,1],[29,1,36,1],[39,1,42,1],[43,1,44,1]]}
["通用分区"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
[null,null,"空间ID","RoomID",null,"Str","S","X"]
[null,null,"空间名称","RoomName",null,"Str","S","X"]
["基本信息",null,"空间本地编码","RoomLocalID",null,"Str","M","B1"]
[null,null,"空间本地名称","RoomLocalName",null,"Str","M","B1"]
[null,null,"空间二维码图片","RoomQRCode",null,"Attachment","R","F2"]
[null,null,"BIM模型中编码","BIMID",null,"Str","R","N2"]
[null,null,"BIM模型中坐标","BIMLocation",null,"Str","R","N2"]
[null,null,"进深","Depth","m","Num","R","A2"]
[null,null,"面宽","Width","m","Num","R","A2"]
[null,null,"建筑面积","BuildArea","m2","Num","M","A2"]
[null,null,"使用面积","NetArea","m2","Num","M","A2"]
[null,null,"高度","Height","m","Num","M","A2"]
[null,null,"备注文字","Intro",null,"Str","R","B2"]
[null,null,"配电容量","ElecCap","A","Num","R","A2"]
[null,null,"污染等级","PollutionDegree",null,"Enum","R","D1","见《12污染等级》","电气间隙或爬电距离的微观环境污染"]
[null,null,"空间功能区类型","RoomFuncType",null,"Enum","S","D1","见《8空间功能类型》"]
["租户信息",null,"租赁业态类型","TenantType",null,"Enum","M","D1","见《9租赁业态类型》"]
[null,null,"所属租户","Tenant",null,"Str","R","B1"]
["环境参数","温湿度","空气（干球）温度","Tdb","℃","Inst","M","L"]
[null,null,"空气相对湿度","RH","%RH","Inst","M","L"]
[null,null,"空气含湿量","D","g/kg.dra","Inst","R","L"]
[null,null,"空气湿球温度","Twb","℃","Inst","R","L"]
[null,null,"空气露点温度","Td","℃","Inst","R","L"]
[null,null,"空气比焓","H","kJ/kg.dra","Inst","R","L"]
[null,null,"空气密度","Rou","kg/m3","Inst","R","L"]
[null,null,"环境黑球温度","Tg","℃","Inst","R","L"]
[null,"压力","空气压力","Press","MPa","Inst","R","L",null,"全压"]
[null,"空气质量","空气CO2浓度","CO2","ppm","Inst","M","L"]
[null,null,"空气CO浓度","CO","ppm","Inst","R","L"]
[null,null,"空气PM2.5浓度","PM2.5","mg/m3","Inst","M","L"]
[null,null,"空气PM10浓度","PM10","mg/m3","Inst","R","L"]
[null,null,"空气烟尘浓度","Dust","mg/m3","Inst","R","L"]
[null,null,"空气VOC浓度","VOC","ppm","Inst","R","L",null,"1ppb=10^-3ppm"]
[null,null,"空气甲烷浓度","CH4","ppm","Inst","R","L",null,"1%LEL=0.0005ppm(CH4)"]
[null,null,"空气质量指数","AQI",null,"Inst","R","L"]
[null,"光照","环境照度","Lux","lux","Inst","M","L"]
[null,"声强","环境噪声","Noise","dB(A)","Inst","M","L"]
[null,"风速","空气平均风速","WindAveV","m/s","Inst","R","L"]
[null,null,"空气X向风速","WindVx","m/s","Inst","R","L"]
[null,null,"空气Y向风速","WindVy","m/s","Inst","R","L"]
[null,null,"空气Z向风速","WindVz","m/s","Inst","R","L"]
[null,"关键指标","热舒适PMV","PMV",null,"Inst","R","M"]
[null,null,"热舒适PPD","PPD",null,"Inst","R","M"]
["人员信息",null,"空间常驻人数","PermanentPeopleNum","人","Num","M","A2"]
[null,null,"逐时流出人数","OutPeopleFlow","人次/min","Inst","R","L"]
[null,null,"逐时流入人数","InPeopleFlow","人次/min","Inst","R","L"]
[null,null,"逐时空间内现有人数","ExsitPeopleNum","人","Inst","R","M"]
["能耗信息","逐时","逐时用电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"逐时用燃气量","GasConsumP","m3/h","Inst","M","L"]
[null,null,"燃气压力","GasPress","Pa","Inst","R","L"]
[null,null,"逐时用燃油量","FuelConsumP","L/h","Inst","R","L"]
[null,null,"燃油压力","FuelPress","MPa","Inst","R","L"]
[null,null,"逐时用水量","WaterConsumP","m3/h","Inst","M","L"]
[null,null,"自来水压力","WaterPress","MPa","Inst","R","L"]
[null,null,"逐时用热量","HeatConsumP","kW","Inst","R","L"]
[null,null,"逐时用冷量","CoolConsumP","kW","Inst","R","L"]
[null,null,"空调水压力","ACWaterPress","MPa","Inst","R","L"]
[null,null,"空调送风压力","ACWindPress","Pa","Inst","R","L"]
[null,null,"逐时用热水量","DHWConsumP","m3/h","Inst","R","L"]
[null,null,"热水压力","DHWPress","MPa","Inst","R","L"]
[null,null,"逐时用蒸汽量","VaporConsumP","m3/h","Inst","R","L"]
[null,null,"蒸汽压力","VaporPress","MPa","Inst","R","L"]
[null,"累计","累计用电量","ElecAccConsum","kWh","Acc","M","L"]
[null,null,"累计用燃气量","GasAccConsum","m3","Acc","M","L"]
[null,null,"累计用燃油量","FuelAccConsum","L","Acc","R","L"]
[null,null,"累计用水量","WaterAccConsum","m3","Acc","M","L"]
[null,null,"累计用热量","HeatAccConsum","kWh","Acc","R","L"]
[null,null,"累计用冷量","CoolAccConsum","kWh","Acc","R","L"]
[null,null,"累计用热水量","DHWAccConsum","m3","Acc","R","L"]
[null,null,"累计用蒸汽量","VaporAccConsum","m3","Acc","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"供电分区","index":2,"n_rows":22,"n_cols":10,"rows_kept":22,"cut":false,"hidden":false,"merged":[[20,0,20,1],[21,0,21,1],[17,0,19,1],[0,0,0,9],[1,0,1,1],[2,0,2,1],[3,0,3,1],[4,0,16,1]]}
["供电分区"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
[null,null,"空间ID","RoomID",null,"Str","S","X"]
[null,null,"空间名称","RoomName",null,"Str","S","X"]
["基本信息",null,"空间本地编码","RoomLocalID",null,"Str","M","B1"]
[null,null,"空间本地名称","RoomLocalName",null,"Str","M","B1"]
[null,null,"空间二维码图片","RoomQRCode",null,"Attachment","R","F2"]
[null,null,"BIM模型中编码","BIMID",null,"Str","R","N2"]
[null,null,"BIM模型中坐标","BIMLocation",null,"Str","R","N2"]
[null,null,"进深","Depth","m","Num","R","A2"]
[null,null,"面宽","Width","m","Num","R","A2"]
[null,null,"建筑面积","BuildArea","m2","Num","M","A2"]
[null,null,"使用面积","NetArea","m2","Num","M","A2"]
[null,null,"高度","Height","m","Num","M","A2"]
[null,null,"备注文字","Intro",null,"Str","R","B2"]
[null,null,"配电容量","ElecCap","A","Num","R","A2"]
[null,null,"污染等级","PollutionDegree",null,"Enum","R","D1","见《12污染等级》","电气间隙或爬电距离的微观环境污染"]
["运行参数",null,"电压","U","V","Inst","M","L"]
[null,null,"总电流","TotI","A","Inst","M","L"]
[null,null,"总电功率","TotP","kW","Inst","M","L"]
["设定参数"]
["报警消息"]

{"sheet":"照明分区","index":3,"n_rows":21,"n_cols":10,"rows_kept":21,"cut":false,"hidden":false,"merged":[[19,0,19,1],[20,0,20,1],[0,0,0,9],[1,0,1,1],[2,0,2,1],[3,0,3,1],[4,0,16,1],[17,0,18,1]]}
["照明分区"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
[null,null,"空间ID","RoomID",null,"Str","S","X"]
[null,null,"空间名称","RoomName",null,"Str","S","X"]
["基本信息",null,"空间本地编码","RoomLocalID",null,"Str","M","B1"]
[null,null,"空间本地名称","RoomLocalName",null,"Str","M","B1"]
[null,null,"空间二维码图片","RoomQRCode",null,"Attachment","R","F2"]
[null,null,"BIM模型中编码","BIMID",null,"Str","R","N2"]
[null,null,"BIM模型中坐标","BIMLocation",null,"Str","R","N2"]
[null,null,"进深","Depth","m","Num","R","A2"]
[null,null,"面宽","Width","m","Num","R","A2"]
[null,null,"建筑面积","BuildArea","m2","Num","M","A2"]
[null,null,"使用面积","NetArea","m2","Num","M","A2"]
[null,null,"高度","Height","m","Num","M","A2"]
[null,null,"备注文字","Intro",null,"Str","R","B2"]
[null,null,"设计照明功率","RatedLightP","kW","Num","M","A2"]
[null,null,"内外区类型","ZoneType",null,"Enum","M","D1","1. 内区 2. 外区 99. 其他"]
["运行参数",null,"工作面照度","WorkPlaneLux","lux","Inst","M","L"]
[null,null,"照明功率","LightP","kW","Inst","M","L"]
["设定参数"]
["报警消息"]

{"sheet":"网络分区","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"空调分区","index":5,"n_rows":48,"n_cols":10,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,2,1],[3,0,3,1],[4,0,17,1],[46,0,46,1],[47,0,47,1],[18,1,41,1],[18,0,45,0],[42,1,45,1]]}
["空调分区"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
[null,null,"空间ID","RoomID",null,"Str","S","X"]
[null,null,"空间名称","RoomName",null,"Str","S","X"]
["基本信息",null,"空间本地编码","RoomLocalID",null,"Str","M","B1"]
[null,null,"空间本地名称","RoomLocalName",null,"Str","M","B1"]
[null,null,"空间二维码图片","RoomQRCode",null,"Attachment","R","F2"]
[null,null,"BIM模型中编码","BIMID",null,"Str","R","N2"]
[null,null,"BIM模型中坐标","BIMLocation",null,"Str","R","N2"]
[null,null,"进深","Depth","m","Num","R","A2"]
[null,null,"面宽","Width","m","Num","R","A2"]
[null,null,"建筑面积","BuildArea","m2","Num","M","A2"]
[null,null,"使用面积","NetArea","m2","Num","M","A2"]
[null,null,"高度","Height","m","Num","M","A2"]
[null,null,"备注文字","Intro",null,"Str","R","B2"]
[null,null,"设计供冷功率","RatedCoolingP","kW","Num","M","A2"]
[null,null,"设计供热功率","RatedHeatingP","kW","Num","M","A2"]
[null,null,"空调形式","ACType",null,"Enum","M","D1","1. 全空气系统 2. 风机盘管 3. 多联机 4. 分体机 99. 其他"]
["运行参数","环境参数","空气（干球）温度","Tdb","℃","Inst","M","L"]
[null,null,"空气相对湿度","RH","%RH","Inst","M","L"]
[null,null,"空气含湿量","D","g/kg.dra","Inst","R","L"]
[null,null,"空气湿球温度","Twb","℃","Inst","R","L"]
[null,null,"空气露点温度","Td","℃","Inst","R","L"]
[null,null,"空气比焓","H","kJ/kg.dra","Inst","R","L"]
[null,null,"空气密度","Rou","kg/m3","Inst","R","L"]
[null,null,"环境黑球温度","Tg","℃","Inst","R","L"]
[null,null,"空气压力","Press","MPa","Inst","R","L",null,"全压"]
[null,null,"空气CO2浓度","CO2","ppm","Inst","M","L"]
[null,null,"空气CO浓度","CO","ppm","Inst","R","L"]
[null,null,"空气PM2.5浓度","PM2.5","mg/m3","Inst","M","L"]
[null,null,"空气PM10浓度","PM10","mg/m3","Inst","R","L"]
[null,null,"空气烟尘浓度","Dust","mg/m3","Inst","R","L"]
[null,null,"空气VOC浓度","VOC","ppm","Inst","R","L",null,"1ppb=10^-3ppm"]
[null,null,"空气甲烷浓度","CH4","ppm","Inst","R","L",null,"1%LEL=0.0005ppm(CH4)"]
[null,null,"空气质量指数","AQI",null,"Inst","R","L"]
[null,null,"环境噪声","Noise","dB(A)","Inst","M","L"]
[null,null,"空气平均风速","WindAveV","m/s","Inst","R","L"]
[null,null,"空气X向风速","WindVx","m/s","Inst","R","L"]
[null,null,"空气Y向风速","WindVy","m/s","Inst","R","L"]
[null,null,"空气Z向风速","WindVz","m/s","Inst","R","L"]
[null,null,"热舒适PMV","PMV",null,"Inst","R","M"]
[null,null,"热舒适PPD","PPD",null,"Inst","R","M"]
[null,"关键指标","逐时用热量","HeatConsumP","kW","Inst","R","L"]
[null,null,"逐时用冷量","CoolConsumP","kW","Inst","R","L"]
[null,null,"空调水压力","ACWaterPress","MPa","Inst","R","L"]
[null,null,"空调送风压力","ACWindPress","Pa","Inst","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"采暖分区","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"洁净分区","index":7,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"生活给水分区","index":8,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"防火分区","index":9,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"安防分区","index":10,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"租户分区","index":11,"n_rows":42,"n_cols":10,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,2,1],[3,0,3,1],[40,0,40,1],[41,0,41,1],[4,0,16,1],[17,0,39,0],[17,1,31,1],[32,1,39,1]]}
["租户分区"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
[null,null,"空间ID","RoomID",null,"Str","S","X"]
[null,null,"空间名称","RoomName",null,"Str","S","X"]
["基本信息",null,"空间本地编码","RoomLocalID",null,"Str","M","B1"]
[null,null,"空间本地名称","RoomLocalName",null,"Str","M","B1"]
[null,null,"空间二维码图片","RoomQRCode",null,"Attachment","R","F2"]
[null,null,"BIM模型中编码","BIMID",null,"Str","R","N2"]
[null,null,"BIM模型中坐标","BIMLocation",null,"Str","R","N2"]
[null,null,"进深","Depth","m","Num","R","A2"]
[null,null,"面宽","Width","m","Num","R","A2"]
[null,null,"建筑面积","BuildArea","m2","Num","M","A2"]
[null,null,"使用面积","NetArea","m2","Num","M","A2"]
[null,null,"高度","Height","m","Num","M","A2"]
[null,null,"备注文字","Intro",null,"Str","R","B2"]
[null,null,"租赁业态类型","TenantType",null,"Enum","M","D1","见《9租赁业态类型》"]
[null,null,"所属租户","Tenant",null,"Str","R","B1"]
["能耗信息","逐时","逐时用电功率","ElecConsumP","kW","Inst","M","L"]
[null,null,"逐时用燃气量","GasConsumP","m3/h","Inst","M","L"]
[null,null,"燃气压力","GasPress","Pa","Inst","R","L"]
[null,null,"逐时用燃油量","FuelConsumP","L/h","Inst","R","L"]
[null,null,"燃油压力","FuelPress","MPa","Inst","R","L"]
[null,null,"逐时用水量","WaterConsumP","m3/h","Inst","M","L"]
[null,null,"自来水压力","WaterPress","MPa","Inst","R","L"]
[null,null,"逐时用热量","HeatConsumP","kW","Inst","R","L"]
[null,null,"逐时用冷量","CoolConsumP","kW","Inst","R","L"]
[null,null,"空调水压力","ACWaterPress","MPa","Inst","R","L"]
[null,null,"空调送风压力","ACWindPress","Pa","Inst","R","L"]
[null,null,"逐时用热水量","DHWConsumP","m3/h","Inst","R","L"]
[null,null,"热水压力","DHWPress","MPa","Inst","R","L"]
[null,null,"逐时用蒸汽量","VaporConsumP","m3/h","Inst","R","L"]
[null,null,"蒸汽压力","VaporPress","MPa","Inst","R","L"]
[null,"累计","累计用电量","ElecAccConsum","kWh","Acc","M","L"]
[null,null,"累计用燃气量","GasAccConsum","m3","Acc","M","L"]
[null,null,"累计用燃油量","FuelAccConsum","L","Acc","R","L"]
[null,null,"累计用水量","WaterAccConsum","m3","Acc","M","L"]
[null,null,"累计用热量","HeatAccConsum","kWh","Acc","R","L"]
[null,null,"累计用冷量","CoolAccConsum","kWh","Acc","R","L"]
[null,null,"累计用热水量","DHWAccConsum","m3","Acc","R","L"]
[null,null,"累计用蒸汽量","VaporAccConsum","m3","Acc","R","L"]
["设定参数"]
["报警消息"]

{"sheet":"功能分区","index":12,"n_rows":22,"n_cols":10,"rows_kept":22,"cut":false,"hidden":false,"merged":[[20,0,20,1],[21,0,21,1],[4,0,15,1],[16,0,19,1],[0,0,0,9],[1,0,1,1],[2,0,2,1],[3,0,3,1]]}
["功能分区"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
[null,null,"空间ID","RoomID",null,"Str","S","X"]
[null,null,"空间名称","RoomName",null,"Str","S","X"]
["基本信息",null,"空间本地编码","RoomLocalID",null,"Str","M","B1"]
[null,null,"空间本地名称","RoomLocalName",null,"Str","M","B1"]
[null,null,"空间二维码图片","RoomQRCode",null,"Attachment","R","F2"]
[null,null,"BIM模型中编码","BIMID",null,"Str","R","N2"]
[null,null,"BIM模型中坐标","BIMLocation",null,"Str","R","N2"]
[null,null,"进深","Depth","m","Num","R","A2"]
[null,null,"面宽","Width","m","Num","R","A2"]
[null,null,"建筑面积","BuildArea","m2","Num","M","A2"]
[null,null,"使用面积","NetArea","m2","Num","M","A2"]
[null,null,"高度","Height","m","Num","M","A2"]
[null,null,"备注文字","Intro",null,"Str","R","B2"]
[null,null,"空间功能区类型","RoomFuncType",null,"Enum","S","D1","见《8空间功能类型》"]
["人员信息",null,"空间常驻人数","PermanentPeopleNum","人","Num","M","A2"]
[null,null,"逐时流出人数","OutPeopleFlow","人次/min","Inst","R","L"]
[null,null,"逐时流入人数","InPeopleFlow","人次/min","Inst","R","L"]
[null,null,"逐时空间内现有人数","ExsitPeopleNum","人","Inst","R","M"]
["设定参数"]
["报警消息"]