{"text_format":"2","workbook":"xlsx","n_sheets":4,"sheets":["List","维保举例","巡检举例","运行举例"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"List","index":0,"n_rows":32,"n_cols":6,"rows_kept":32,"cut":false,"hidden":false,"merged":[[0,1,0,5],[1,1,1,3],[2,1,2,3],[3,1,3,3],[9,1,9,3],[4,1,4,3],[10,1,28,1],[10,2,15,2],[16,2,21,2],[23,2,28,2],[5,1,5,3],[8,1,8,3],[6,1,6,3],[7,1,7,3]]}
[null,"通用"]
[null,"编码",null,null,"Str","有规则"]
[null,"名称",null,null,"Str","有规则"]
[null,"专业",null,null,"Enum","引用“数据字典”专业分类"]
[null,"类型",null,null,"Enum","维保、运行、巡检、维修、安防..."]
[null,"对象",null,null,"Object","引用“数据字典”对象"]
[null,"周期",null,null,"Num","与时间有连接考虑"]
[null,"每次开始时间",null,null,"Num","与频率有连接考虑"]
[null,"地点",null,null,"空间Object","与对象有连接"]
[null,"重要性",null,null,"Enum","高级、中级、低级…"]
[null,"操作流程",1,"操作前提确认","Str","或信息点数据逻辑"]
[null,null,null,"操作内容","Str"]
[null,null,null,"操作步骤对象","Object","引用“数据字典”对象"]
[null,null,null,"操作工具","Object或Str","引用“数据字典”工具对象"]
[null,null,null,"操作结果确认","Str","需采集（Num或Enum）"]
[null,null,null,"注意事项","Str"]
[null,null,2,"操作前提确认"]
[null,null,null,"操作内容"]
[null,null,null,"操作对象"]
[null,null,null,"操作工具"]
[null,null,null,"操作结果确认"]
[null,null,null,"注意事项"]
[null,null,"……"]
[null,null,"n","操作前提确认"]
[null,null,null,"操作内容"]
[null,null,null,"操作对象"]
[null,null,null,"操作工具"]
[null,null,null,"操作结果确认"]
[null,null,null,"注意事项"]
[]
[]
[{"$nulls":5},"是否有严格顺序规定如何表示？"]

{"sheet":"维保举例","index":1,"n_rows":178,"n_cols":4,"rows_kept":178,"cut":false,"hidden":false,"merged":[[166,1,171,1],[160,1,165,1],[124,1,129,1],[5,0,5,2],[0,0,0,3],[1,0,1,2],[2,0,2,2],[4,0,4,2],[88,1,93,1],[94,1,99,1],[100,1,105,1],[70,1,75,1],[6,0,6,2],[9,0,9,2],[10,0,177,0],[10,1,15,1],[16,1,21,1],[172,1,177,1],[22,1,27,1],[28,1,33,1],[34,1,39,1],[40,1,45,1],[46,1,51,1],[52,1,57,1],[3,0,3,2],[7,0,7,2],[8,0,8,2],[76,1,81,1],[82,1,87,1],[58,1,63,1],[64,1,69,1],[154,1,159,1],[148,1,153,1],[142,1,147,1],[136,1,141,1],[106,1,111,1],[118,1,123,1],[112,1,117,1],[130,1,135,1]]}
["维保"]
["编码",null,null,"AC-001"]
["名称",null,null,"月度空调维保"]
["类型",null,null,"维保"]
["专业",null,null,"空调"]
["对象",null,null,"离心机"]
["周期",null,null,"每月"]
["每次开始日期（时间）",null,null,"1日"]
["地点",null,null,"冷站"]
["重要性",null,null,"一般（日常）"]
["操作流程",1,"操作前提确认"]
[null,null,"操作内容","检查并报告任何异常噪音或震动"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,2,"操作前提确认"]
[null,null,"操作内容","检查连接处，防止漏水检查是否漏油"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,3,"操作前提确认"]
[null,null,"操作内容","打开配电板和控制面板，检查有无接触不良导致氧化现象"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,4,"操作前提确认"]
[null,null,"操作内容","检查温度计和压力计是否处于正常工作状态"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,5,"操作前提确认"]
[null,null,"操作内容","检查密封状况并在必要时予以更换"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,6,"操作前提确认"]
[null,null,"操作内容","检验管道的紧密度"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,7,"操作前提确认"]
[null,null,"操作内容","检查冷冻机油油位"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,8,"操作前提确认"]
[null,null,"操作内容","检查冷媒控件和安全装置"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,9,"操作前提确认"]
[null,null,"操作内容","检查螺栓和螺钉"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,10,"操作前提确认"]
[null,null,"操作内容","在必要的地方添加冷媒和油脂"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具","冷媒，油脂"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,11,"操作前提确认"]
[null,null,"操作内容","跟踪压缩机启动电流，报告任何异常状况"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,12,"操作前提确认"]
[null,null,"操作内容","检查电气设备，确保其常规运作良好"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,13,"操作前提确认"]
[null,null,"操作内容","检查、清洁、调整控制设备"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,14,"操作前提确认"]
[null,null,"操作内容","对接触点、轴承、自动阀门进行必要的润滑"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具","润滑油"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,15,"操作前提确认"]
[null,null,"操作内容","检查电线和电气零部件状况"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,16,"操作前提确认"]
[null,null,"操作内容","检查启动器接触点状况"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,17,"操作前提确认"]
[null,null,"操作内容","检查所有安全和温度控件的安装完整性"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,18,"操作前提确认"]
[null,null,"操作内容","检查管架和连接点的外观"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,19,"操作前提确认"]
[null,null,"操作内容","检查独立阀门和电动开关阀是否正常运作"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,20,"操作前提确认"]
[null,null,"操作内容","清洁冷却水系统的水过滤器（如安装）"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,21,"操作前提确认"]
[null,null,"操作内容","检查金属组件是否腐蚀，必要时用钢丝刷清洁金属"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具","钢丝刷"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,22,"操作前提确认"]
[null,null,"操作内容","并使用标准防腐涂料喷涂其表面"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具","防腐涂料"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,23,"操作前提确认"]
[null,null,"操作内容","检查绝缘材料状况，必要时予以更换"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具","绝缘材料"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,24,"操作前提确认"]
[null,null,"操作内容","检查所有控件、延时和安全装置的设定点是否异常，必要时重置不正确参数"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,25,"操作前提确认"]
[null,null,"操作内容","检查曲轴箱加热器，确保其正常运行，必要时用油脂润滑防振器"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具","油脂"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,25,"操作前提确认"]
[null,null,"操作内容","润滑外露阀轴，防止生锈"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,25,"操作前提确认","如已安装楼宇自控系统，在远程控制状态下"]
[null,null,"操作内容","校验制冷机的作业序列"]
[null,null,"操作步骤对象","离心机"]
[null,null,"操作工具"]
[null,null,"操作结果确认"]
[null,null,"注意事项"]
[null,27,"操作前提确认"]
[null,null,"操作内容","测量并记录主要运行参数，包括压缩机流，冷媒压力，冷冻水的内外压差等"]
[null,null,"操作步骤对象"]
[null,null,"操作工具"]
[null,null,"操作结果确认","确保运行参数与运行条件相符"]
[null,null,"注意事项"]

{"sheet":"巡检举例","index":2,"n_rows":136,"n_cols":4,"rows_kept":136,"cut":false,"hidden":false,"merged":[[76,1,81,1],[70,1,75,1],[124,1,129,1],[118,1,123,1],[112,1,117,1],[106,1,111,1],[10,0,135,0],[10,1,15,1],[16,1,21,1],[130,1,135,1],[64,1,69,1],[58,1,63,1],[52,1,57,1],[46,1,51,1],[40,1,45,1],[28,1,33,1],[22,1,27,1],[100,1,105,1],[94,1,99,1],[88,1,93,1],[82,1,87,1],[34,1,39,1],[3,0,3,2],[8,0,8,2],[9,0,9,2],[6,0,6,2],[0,0,0,3],[1,0,1,2],[2,0,2,2],[4,0,4,2],[5,0,5,2],[7,0,7,2]]}
["巡检"]
["编码",null,null,"AC-XJ-01"]
["名称",null,null,"冷冻站巡检"]
["类型",null,null,"巡检"]
["专业",null,null,"空调"]
["对象",null,null,"冷冻站设备"]
["周期",null,null,"4次/日"]
["每次开始时间",null,null,"07:00-09:00,09:00-12:00,12:00-15:00,15:00-23:00"]
["地点",null,null,"冷站"]
["重要性",null,null,"一般（日常）"]
["巡检流程",1,"操作前提确认"]
[null,null,"操作内容","检查各类设备开启台数匹配"]
[null,null,"操作步骤对象","冷冻站设备"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,2,"操作前提确认"]
[null,null,"操作内容","检查冷机高压情况"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值（<850kPa为正常）"]
[null,null,"注意事项"]
[null,3,"操作前提确认"]
[null,null,"操作内容","检查冷机低压情况"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值（>210kPa为正常）"]
[null,null,"注意事项"]
[null,4,"操作前提确认"]
[null,null,"操作内容","检查冷却水进水温度"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值（<27-32℃为正常）"]
[null,null,"注意事项"]
[null,5,"操作前提确认"]
[null,null,"操作内容","检查冷却水出水温度"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值（<32-37℃为正常）"]
[null,null,"注意事项"]
[null,6,"操作前提确认"]
[null,null,"操作内容","检查冷却水压差"]
[null,null,"操作步骤对象","冷却水泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,7,"操作前提确认"]
[null,null,"操作内容","检查冷却水泵运转是否正常"]
[null,null,"操作步骤对象","冷却水泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,8,"操作前提确认"]
[null,null,"操作内容","检查冷冻水供水温度"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值（与设计值一致为正常）"]
[null,null,"注意事项"]
[null,9,"操作前提确认"]
[null,null,"操作内容","检查冷冻水回水温度"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值（与设计值一致为正常）"]
[null,null,"注意事项"]
[null,10,"操作前提确认"]
[null,null,"操作内容","检查冷冻水压差"]
[null,null,"操作步骤对象","冷冻水泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,11,"操作前提确认"]
[null,null,"操作内容","检查冷冻水泵运转是否正常"]
[null,null,"操作步骤对象","冷冻水泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,12,"操作前提确认"]
[null,null,"操作内容","检查水处理设备运转是否正常"]
[null,null,"操作步骤对象","水处理设备"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,13,"操作前提确认"]
[null,null,"操作内容","检查集水器温度"]
[null,null,"操作步骤对象","集水器"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,14,"操作前提确认"]
[null,null,"操作内容","检查集水器压力"]
[null,null,"操作步骤对象","集水器"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,15,"操作前提确认"]
[null,null,"操作内容","检查分水器温度"]
[null,null,"操作步骤对象","分水器"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,16,"操作前提确认"]
[null,null,"操作内容","检查分水器压力"]
[null,null,"操作步骤对象","分水器"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,17,"操作前提确认"]
[null,null,"操作内容","检查管道阀门是否漏水"]
[null,null,"操作步骤对象","管道阀门"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,18,"操作前提确认"]
[null,null,"操作内容","检查软接头是否异常拉伸"]
[null,null,"操作步骤对象","软接头"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,19,"操作前提确认"]
[null,null,"操作内容","检查控制柜（箱）情况"]
[null,null,"操作步骤对象","控制柜（箱）"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,20,"操作前提确认"]
[null,null,"操作内容","检查保温是否完好"]
[null,null,"操作步骤对象","保温"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,21,"操作前提确认"]
[null,null,"操作内容","检查卫生情况"]
[null,null,"操作步骤对象","冷冻站"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]

{"sheet":"运行举例","index":3,"n_rows":106,"n_cols":4,"rows_kept":106,"cut":false,"hidden":false,"merged":[[94,1,99,1],[88,1,93,1],[82,1,87,1],[1,0,1,2],[2,0,2,2],[4,0,4,2],[5,0,5,2],[10,0,105,0],[10,1,15,1],[16,1,21,1],[100,1,105,1],[76,1,81,1],[0,0,0,3],[70,1,75,1],[64,1,69,1],[58,1,63,1],[52,1,57,1],[46,1,51,1],[40,1,45,1],[34,1,39,1],[28,1,33,1],[22,1,27,1],[3,0,3,2],[6,0,6,2],[7,0,7,2],[9,0,9,2],[8,0,8,2]]}
["运行"]
["编码",null,null,"AC-YX-01"]
["名称",null,null,"冷冻站开机操作规程"]
["类型",null,null,"运行"]
["专业",null,null,"空调"]
["对象",null,null,"冷冻站设备"]
["周期",null,null,"供冷季每天一次"]
["每次开始时间",null,null,"07:00:00"]
["地点",null,null,"冷冻站"]
["重要性",null,null,"一般（日常）"]
["操作流程",1,"操作前提确认"]
[null,null,"操作内容","根据室外温度，确定冷冻机开机台数"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,2,"操作前提确认"]
[null,null,"操作内容","检查冷却水侧手动阀门是否已打开"]
[null,null,"操作步骤对象","冷却水手动阀"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,3,"操作前提确认"]
[null,null,"操作内容","开启冷冻机冷却水侧电动阀"]
[null,null,"操作步骤对象","冷却水电动阀"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,4,"操作前提确认"]
[null,null,"操作内容","开启冷却塔电动阀"]
[null,null,"操作步骤对象","冷却塔电动阀"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,5,"操作前提确认"]
[null,null,"操作内容","开启冷却水泵"]
[null,null,"操作步骤对象","冷却泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,6,"操作前提确认"]
[null,null,"操作内容","检查冷冻水侧手动阀门是否已打开"]
[null,null,"操作步骤对象","冷冻水手动阀"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,7,"操作前提确认"]
[null,null,"操作内容","开启冷冻机冷冻水侧电动阀"]
[null,null,"操作步骤对象","冷冻水电动阀"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,8,"操作前提确认"]
[null,null,"操作内容","开启冷冻水一次泵"]
[null,null,"操作步骤对象","一次泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,9,"操作前提确认"]
[null,null,"操作内容","开启冷冻水二次泵"]
[null,null,"操作步骤对象","二次泵"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,10,"操作前提确认"]
[null,null,"操作内容","开启冷却塔"]
[null,null,"操作步骤对象","冷却塔"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,11,"操作前提确认"]
[null,null,"操作内容","开启冷水机组"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项","以上步骤均正常时"]
[null,12,"操作前提确认"]
[null,null,"操作内容","设置冷冻水供水温度"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,13,"操作前提确认"]
[null,null,"操作内容","记录冷却水温度"]
[null,null,"操作步骤对象","冷机"]
[null,null,"操作工具"]
[null,null,"操作结果确认","数值"]
[null,null,"注意事项"]
[null,14,"操作前提确认"]
[null,null,"操作内容","检查开启设备是否运行正常"]
[null,null,"操作步骤对象","冷冻站设备"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,15,"操作前提确认"]
[null,null,"操作内容","检查管道阀门是否漏水"]
[null,null,"操作步骤对象","管道阀门"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]
[null,16,"操作前提确认"]
[null,null,"操作内容","检查软接头是否异常拉伸"]
[null,null,"操作步骤对象","软接头"]
[null,null,"操作工具"]
[null,null,"操作结果确认","是否正常"]
[null,null,"注意事项"]