{"text_format":"2","workbook":"xlsx","n_sheets":11,"sheets":["DW生活给水系统","DH生活热水系统","RW中水系统","DD直饮水系统","ST污水处理系统","SI喷灌系统","WS水景系统","WP泳池系统","FG燃气系统","WH给排水电伴热系统","WD给排水人防系统"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"DW生活给水系统","index":0,"n_rows":31,"n_cols":10,"rows_kept":31,"cut":false,"hidden":false,"merged":[[29,0,29,1],[30,0,30,1],[0,0,0,9],[1,0,1,1],[17,0,28,0],[2,0,16,1],[17,1,26,1],[27,1,28,1]]}
["生活给水系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"系统是否高低分区","isHighLowZone",null,"Bool","S","E1","0. 单区域系统 1. 多区域系统"]
[null,null,"是否有蓄水池","isReservoir",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"是否有上水箱 ","isUpTank",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有减压阀","isReduceValve",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有消毒器","isSterilizer",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"消毒器类型","SterilizerType",null,"Enum","R","D1","1. 水箱自洁消毒 2. 紫外线消毒器 99. 其他"]
[null,null,"是否有供水机组","isSupplyUnit",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"供水机组类型","SupplyUnitType",null,"Enum","M","D1","1. 重力式供水机组 2. 气罐式供水机组 3. 变频恒压供水系统 4. 无负压叠压供水系统 5. 补水式无负压供水机组 99. 其他"]
[null,null,"定压方式","ConstantPressType",null,"Enum","R","D1","1. 水箱定压 2. 泵定压 3. 气罐定压 99. 其他"]
[null,null,"供水分区","SupplyZoneType",null,"Enum","S","D1","1. 二区（高区、低区） 2. 三区（高区、中区、低区） 99. 其他","多区域系统"]
[null,null,"两区域供水机组连接形式","2PartSupplyUnitConnectType",null,"Enum","S","D1","1. 低区市政直供，高区供水机组 2. 低区高区各自供水机组 3. 低区总泵，高区加压泵 99. 其他","两区域系统"]
[null,null,"三区域供水机组连接形式","3PartSupplyUnitConnectType",null,"Enum","S","D1","1. 低区市政直供，中区高区各自供水机组 2. 低区市政直供，中区总泵，高区加压泵 3. 低区中区高区各自供水机组 4. 低区总泵，中区高区各自加压泵 5. 低区总泵，中区加压泵，高区二次加压泵 99. 其他","三区域系统"]
[null,null,"最大供水量","MaxSupplyFlow","m3/h","Num","S","A2"]
[null,null,"供水户数","UserNum","户","Num","M","A2"]
[null,null,"最不利环路压降","RatedWorstTerminalPressDrop","MPa","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","S","M"]
[null,null,"瞬时用水量","WaterConsumFlow","m3/h","Inst","S","L"]
[null,null,"瞬时净化水量","WaterPurifyFlow","m3/h","Inst","R","L"]
[null,null,"市政水入口压力","MunicipalPress","MPa","Inst","M","L"]
[null,null,"机组出口供水压力","SupplyUnitOutPress","MPa","Inst","M","L",null,"泵出口压力"]
[null,null,"最不利末端出水压力","WorstTerminalOutPress","Pa","Inst","M","L"]
[null,"累计指标","累计耗电量","AccElecConsum","kWh","Acc","M","M"]
[null,null,"累计用水量","AccWaterConsum","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"DH生活热水系统","index":1,"n_rows":69,"n_cols":10,"rows_kept":69,"cut":false,"hidden":false,"merged":[[67,0,67,1],[68,0,68,1],[31,1,59,1],[0,0,0,9],[1,0,1,1],[31,0,66,0],[62,1,66,1],[21,1,30,1],[2,0,30,0],[2,1,20,1],[60,1,61,1]]}
["生活热水系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","整体","热源","HeatSourceType",null,"MEnum","S","D2","1. 燃油热水锅炉 2. 燃气热水锅炉 3. 电热水锅炉 4. 太阳能热水器 5. 燃气热水器 6. 电热水器 7. 热泵 99. 其他（可多选）"]
[null,null,"系统循环方式","CycleType",null,"Enum","S","D1","1. 全循环系统 2. 半循环系统 3. 不循环直流系统 99. 其他"]
[null,null,"定压方式","ConstantPressType",null,"Enum","R","D1","1. 水箱定压 2. 泵定压 3. 气罐定压 99. 其他"]
[null,null,"是否为机械动力循环","isMachanicalPower",null,"Bool","S","E1","0. 自然循环系统 1. 强制循环系统"]
[null,null,"是否有换热器间接换热","isHeatExchanger",null,"Bool","M","E1","0. 无换热器直供 1. 有换热器间供"]
[null,null,"是否有储热水箱","isHotWaterStoreTank",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"储热水箱容积","HotWaterStoreTankCap","m3","Num","M","A2"]
[null,null,"额定热源出水温度","RatedHeatSourceOutTemp","℃","Num","M","A2"]
[null,null,"额定储热水箱温度","RatedHotWaterStoreTankTemp","℃","Num","M","A2"]
[null,null,"额定供热水温度","RatedSupplyTemp","℃","Num","S","A2"]
[null,null,"额定热源出水流量","RatedHeatSourceOutFlow","m3/h","Num","M","A2"]
[null,null,"额定供热水循环流量","RatedSupplyFlow","m3/h","Num","S","A2"]
[null,null,"最大供热水量","MaxSupplyFlow","m3/h","Num","M","A2"]
[null,null,"热源侧水泵台数","HeatSourcePumpNum","台","Num","M","A2"]
[null,null,"供水侧水泵台数","SupplyPumpNum","台","Num","M","A2"]
[null,null,"供热水户数","UserNum","户","Num","M","A2"]
[null,null,"设计最不利末端压降","RatedWorstTerminalPressDrop","MPa","Num","M","A2"," ","额定流量下"]
[null,null,"混水形式","MixType",null,"Enum","R","D1","1. 无混合装置的直接连接 2. 水喷射器的直接连接 3. 混合水泵的直接连接 99. 其他","无换热器直供"]
[null,null,"换热器形式","HeatExchangerType",null,"Enum","R","D1","1. 板式换热器 2. 容积式换热器 99. 其他","有换热器间供"]
[null,"太阳能","集热器类型","CollectorType",null,"Enum","S","D1","1. 平板型 2. 真空管型 99. 其他"]
[null,null,"集热板与水平方向夹角","CollectorHorizontalAngle","°","Num","R","A2"]
[null,null,"集热板朝向","CollectorDirect",null,"Enum","R","D1","见《6方向代码》"]
[null,null,"有效集热面积","CollectArea","m2","Num","M","A2"]
[null,null,"额定集热器集热效率","RatedCollectEff","%","Num","R","A2"]
[null,null,"集热器间连接形式","CollectorConnect ",null,"Enum","R","D1","1. 串联 2. 并联 99. 其他"]
[null,null,"集热器内传热工质与大气连接形式","CollectorMediumConnect",null,"Enum","R","D1","1. 开口式 2. 敞开式 3. 封闭式 99. 其他"]
[null,null,"是否有辅助热源","isAuxiliaryHeat",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"辅助热源形式","AuxiliaryHeatType",null,"Enum","M","D1","1. 电加热 2. 盘管换热 99. 其他"]
[null,null,"辅助热源最大加热功率","MaxAuxiliaryHeatP","kW","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","S","M"]
[null,null,"供热水温度","HotWaterSupplyTemp","℃","Inst","S","L"]
[null,null,"供热水流量","HotWaterSupplyFlow","m3/h","Inst","M","L"]
[null,null,"热水使用量","HotWaterConsumFlow ","m3/h","Inst","M","M"]
[null,null,"热源出水量","HeatSourceOutFlow","m3/h","Inst","M","L"]
[null,null,"热源出水温度","HeatSourceOutTemp","℃","Inst","M","L"]
[null,null,"热源回水量","HeatSourceReturnFlow","m3/h","Inst","M","L"]
[null,null,"热源回水温度","HeatSourceReturnTemp","℃","Inst","M","L"]
[null,null,"集热器内温度","CollectorTemp","℃","Inst","M","L",null,"太阳能系统"]
[null,null,"辅热设备加热功率","AuxiliaryHeatP","kW","Inst","M","L",null,"太阳能系统"]
[null,null,"储热水箱水量","HotWaterTankVolume","m3","Inst","M","L"]
[null,null,"储热水箱温度","HotWaterTankTemp","℃","Inst","M","L"]
[null,null,"供热水回水温度","HotWaterReturnTemp","℃","Inst","M","L"]
[null,null,"供热水回水流量","HotWaterReturnFlow","m3/h","Inst","M","L"]
[null,null,"市政冷水温度","TapWaterTemp","℃","Inst","R","L"]
[null,null,"冷水补水量","TapWaterFillingFlow","m3/h","Inst","R","L"]
[null,null,"市政冷水入口压力","TapWaterInPress","MPa","Inst","R","L"]
[null,null,"热源侧水泵开启台数","HeatSourcePumpRunNum","台","Inst","S","M"]
[null,null,"供水侧水泵开启台数","SupplyPumpRunNum","台","Inst","S","M"]
[null,null,"热源侧水泵进口压强","HeatSourcePumpInPress","MPa","Inst","M","L"]
[null,null,"热源侧水泵出口压强","HeatSourcePumpOutPress","MPa","Inst","M","L"]
[null,null,"供水侧水泵进口压强","SupplyPumpInPress","MPa","Inst","M","L"]
[null,null,"供水侧水泵出口压强","SupplyPumpOutPress","MPa","Inst","M","L"]
[null,null,"开启热水户数","InstUserNum","户","Inst","R","L"]
[null,null,"最不利末端出水压力","WorstTerminalOutPress","Pa","Inst","M","L"," "]
[null,"瞬时指标","集热器效率","CollectorEff","%","Inst","R","M",null,"太阳能系统"]
[null,null,"系统加热效率","SysEff","%","Inst","R","M"]
[null,"累计指标","系统累计耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计吸收太阳能","AccAbsorbSolarE","kWh","Acc","R","M",null,"太阳能系统"]
[null,null,"累计加热量","AccHeat","kWh","Acc","M","M"]
[null,null,"累计用热水热量","AccHotWaterConsumHeat","kWh","Acc","M","M"]
[null,null,"累计用热水量","AccHotWaterConsumVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"RW中水系统","index":2,"n_rows":37,"n_cols":10,"rows_kept":37,"cut":false,"hidden":false,"merged":[[35,0,35,1],[36,0,36,1],[2,0,22,0],[0,0,0,9],[1,0,1,1],[23,0,34,0],[8,1,22,1],[2,1,7,1],[23,1,31,1],[32,1,34,1]]}
["中水系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","供水","有无市政中水管网","isMunicipalReclaimedWater",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"水源类型","WaterSourceType",null,"MEnum","M","D2","1. 优质杂排水 2. 一般杂排水 3. 生活污水 4. 市政污水 5. 雨水 99.其他（可多选）"]
[null,null,"系统类型","SysType",null,"Enum","R","D1","1. 全部完全分流系统 2. 部分完全分流 3. 无分流简化系统 99. 其他"]
[null,null,"供水机组类型","SupplyUnitType",null,"Enum","M","D1","1. 中水变频供水机组 2. 无负压中水供水机组 99. 其他"]
[null,null,"机组额定供水压力","RatedSupplyPress","MPa","Num","M","A2"]
[null,null,"中水使用途径","UseType",null,"MEnum","S","D2","1. 绿化灌溉 2. 消防 3. 洗车 99. 其他（可多选）"]
[null,"水处理","是否有集水池","isCollectBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有配水池","isDistributeBasin ",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有消毒器","isSterilizer",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有水加药装置","isChemicalFeedEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有物化处理","isPhysicalChemicalTreat",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有生物处理","isBiologyTreat",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有二级生物处理","isSecondaryBiologyTreat",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有调节沉淀池","isAdjustPrecipitationBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有二级沉淀池","isSecondaryPrecipitationBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有活性炭处理","isActiveCarbonTreat",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"过滤器反洗频率","FilterBackwashFreq","次/天","Num","R","A2"]
[null,null,"中水处理能力","RatedReclaimedWaterTreatFlow","m3/h","Num","M","A2"]
[null,null,"集水坑数量","CollectBasinNum","个","Num","R","A2"]
[null,null,"集水坑总容量 ","CollectBasinTotCap","m3","Num","R","A2"]
[null,null,"中水池容量","ReclaimedWaterBasinCap","m3","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"瞬时处理中水量","ReclaimedWaterTreatFlow","m3/h","Inst","M","L"]
[null,null,"瞬时使用中水量","ReclaimedWaterConsumFlow","m3/h","Inst","M","L"]
[null,null,"机组供水压力","SupplyPress","MPa","Inst","M","L"]
[null,null,"中水池水量","ReclaimedWaterBasinVolume","m3","Inst","R","L"]
[null,"累计指标","系统累计耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计处理中水量","AccReclaimedWaterTreatVolume","m3","Acc","M","M"]
[null,null,"累计使用中水量","AccReclaimedWaterConsumVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"DD直饮水系统","index":3,"n_rows":51,"n_cols":10,"rows_kept":51,"cut":false,"hidden":false,"merged":[[49,0,49,1],[50,0,50,1],[0,0,0,9],[1,0,1,1],[2,0,31,0],[32,0,48,0],[27,1,31,1],[2,1,16,1],[17,1,26,1],[32,1,45,1],[46,1,48,1]]}
["直饮水系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","供水","额定处理直饮水量","RatedDrinkWaterTreatFlow","m3/h","Num","S","A2"]
[null,null,"是否有净水箱","isPurifyTank",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"净水箱容积","PurifyTankCap","m3","Num","M","A2"]
[null,null,"是否有原水箱","isRawTank",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"原水箱容积","RawTankCap","m3","Num","M","A2"]
[null,null,"原水泵台数","RawPumpNum","台","Num","M","A2"]
[null,null,"循环泵台数","DrinkPumpNum","台","Num","M","A2"]
[null,null,"机组额定供水压力","RatedSupplyPress","MPa","Num","S","A2"]
[null,null,"循环回水点","CycleReturnNode",null,"Enum","S","D1","1. 原水箱 2. 净水箱 99. 其他"]
[null,null,"额定循环水量","RatedCycleFlow","m3/h","Num","S","A2"]
[null,null,"是否高低分区","isHighLowPart",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"分区供水方式","ZoneSupplyType",null,"Enum","R","D1","1. 水泵并列式 2. 总管减压阀式 3. 支管减压阀式 99. 其他"]
[null,null,"额定最不利末端出水压力","RatedWorstTerminalOutPress","Pa","Num","M","A2",null,"额定水量下"]
[null,null,"是否有末端加热","isTerminalHeat",null,"Bool","S","E1","0. 无 1. 有"]
[null,null,"末端最大加热功率","MaxTerminalHeatP","kW","Num","M","A2"]
[null,"水处理","是否有多介质过滤","isMultimediumFilt",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有活性炭过滤","isActiveCarbonFilt",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有紫外线消毒","isUVSterilize",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有臭氧消毒","isOzoneSterilize",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有软水处理器","isSoftProcessor",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有精密过滤器","isPrecisionFilt",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有pp纤维滤芯装置","isPPFibreFiltEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有反渗透（RO）装置","isROEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有Na膜","isNaFilm",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"膜排列方式","FilmLayoutType",null,"Enum","R","D1","1. 两段式 2. 三段式 99. 其他"]
[null,"水质要求","直饮水色度要求","DrinkWaterChroma",null,"Num","M","A2"]
[null,null,"直饮水浊度要求","DrinkWaterTurbidity","NTU","Num","M","A2"]
[null,null,"直饮水总硬度要求","DrinkWaterHardness","mg/L","Num","M","A2"]
[null,null,"直饮水溶解性总固体要求","DrinkWaterDissolvedSolid","mg/L","Num","M","A2"]
[null,null,"直饮水PH值要求","DrinkWaterPH",null,"Numr","M","A1"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"瞬时净化直饮水量","DrinkWaterTreatFlow","m3/h","Inst","M","L"]
[null,null,"瞬时使用直饮水量","DrinkWaterConsumFlow","m3/h","Inst","M","M"]
[null,null,"直饮水送水量","DrinkWaterSupplyFlow","m3/h","Inst","M","L"]
[null,null,"直饮水回水量","DrinkWaterReturnFlow","m3/h","Inst","M","L"]
[null,null,"机组供水压力","SupplyPress","MPa","Inst","S","L"]
[null,null,"最不利末端出水压力","WorstTerminalOutPress","Pa","Inst","M","L"]
[null,null,"原水箱水量","RawTankVolume","m3","Inst","S","L"]
[null,null,"净水箱水量","PurifyTankVolume","m3","Inst","S","L"]
[null,null,"出口水温","SupplyTemp","℃","Inst","R","L"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计净化直饮水量","AccDrinkWaterTreatVolume","m3","Acc","M","M"]
[null,null,"累计使用直饮水量","AccDrinkWaterConsumVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"ST污水处理系统","index":4,"n_rows":41,"n_cols":10,"rows_kept":41,"cut":false,"hidden":false,"merged":[[39,0,39,1],[40,0,40,1],[0,0,0,9],[1,0,1,1],[28,0,38,0],[2,0,27,0],[11,1,22,1],[23,1,27,1],[2,1,10,1],[28,1,36,1],[37,1,38,1]]}
["污水处理系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","排水","废水类型","WasteWaterType",null,"Enum","S","D1","1. 危废 2. 非危废 3. 可回收废水 4. 餐饮废水 5. 生活污水 99. 其他"]
[null,null,"最大处理能力","MaxTreatCap","m3/天","Num","S","A2"]
[null,null,"潜污泵台数","SubmersibleSewagePumpNum","台","Num","M","A2"]
[null,null,"潜污泵是否耐高温","isSubmersibleSewagePumpHighTempResistance",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"潜污泵是否有切割能力","isSubmersibleSewagePumpCutFunc",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"提升泵台数","LiftPumpNum","台","Num","M","A2"]
[null,null,"是否有一体化泵提升设备","isIntegratedLiftEquip",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"储水箱容量","WasteWaterBasinCap","m3","Num","M","A2",null,"在水质处理结束后，排放入市政管网之前的水箱"]
[null,null,"净化周期","RatedPurifyPeriod","天","Num","R","A2"]
[null,"水处理","处理方法","TreatType",null,"MEnum","S","D2","1. 生物滤池 2. 生物吸附法 3. 污泥水分 99. 其他（可多选）"]
[null,null,"处理级别","TreatLev",null,"Enum","S","D1","1. 一级强化 2. 二级 3. 二级强化 4. 废水回用 99. 其他"]
[null,null,"是否有餐饮除油一体化设备","isIntegratedLampblackEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有潜水曝气机","isSubmergedAerator",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有隔油井","isGreaseInterceptor",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有降温池","isCoolBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有接触氧化池","isOxidationBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有沉淀池","isPrecipitationBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有二沉池","isSecondaryPrecipitationBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有SBR反应池","isSBRReactBasin",null,"Bool","R","E1","0. 无 1. 有","一种间歇曝气的方法"]
[null,null,"是否有CASS池","isCASSBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有消毒池","isSterilizeBasin",null,"Bool","R","E1","0. 无 1. 有","曝气沉淀在一起（循环式活性污泥法）"]
[null,"排放标准","PH值","EmissionPH",null,"Num","M","A1"]
[null,null,"CODcr","EmissionCODcr","mg/L","Num","M","A2",null,"化学需氧量"]
[null,null,"BOD5","EmissionBOD5","mg/L","Num","M","A2",null,"生物需氧量"]
[null,null,"SS","EmissionSS","mg/L","Num","M","A2",null,"悬浮物"]
[null,null,"石油类","EmissionOil","mg/L","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"粗格栅处污水温度","GridWasteWaterTemp","℃","Inst","M","L"]
[null,null,"粗格栅处污水流量","GridWasteWaterFlow","m3/h","Inst","R","L"]
[null,null,"潜污泵开启台数","SubmersibleSewagePumpRunNum ","台","Inst","S","M"]
[null,null,"提升泵开启台数","LiftPumpRunNum","台","Inst","S","M"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计污水处理量","AccWasteWaterTreatVolume","m3","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"SI喷灌系统","index":5,"n_rows":28,"n_cols":10,"rows_kept":28,"cut":false,"hidden":false,"merged":[[23,0,23,1],[24,0,24,1],[0,0,0,9],[15,0,22,0],[1,0,1,1],[2,0,14,0],[6,1,14,1],[2,1,5,1],[15,1,20,1],[21,1,22,1]]}
["喷灌系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","供水","水源","WaterSourceType",null,"Enum","S","D1","1. 地上水 2. 井泉 3. 自来水 4. 中水 99. 其他"]
[null,null,"额定供水压力","RatedSupplyPress","MPa","Num","M","A2"]
[null,null,"压力方式","PressType",null,"Enum","R","D1","1. 机压式 2. 自压式 3. 提水蓄能式 99. 其他"]
[null,null,"管道是否分支","isBr",null,"Bool","R","E1","0. 否 1. 是"]
[null,"末端","是否有雨量感应器","isRainSensor",null,"Bool","M","E1","0. 无 1. 有"]
[null,null,"喷灌控制","SprayMode",null,"Enum","R","D1","1. 定周期喷灌 2. 结合雨量感应器喷灌 99. 其他"]
[null,null,"喷灌周期","RatedSprayPeriod","h","Num","M","A2"]
[null,null,"系统类型","SysType",null,"Enum","R","D1","1. 固定管道式 2. 半固定管道式 3. 移动管道式 99. 其他"]
[null,null,"喷头类型","NozzleType",null,"MEnum","R","D2","1. 旋转式 2. 固定式 3. 孔管式 99. 其他 (可多选)"]
[null,null,"喷头射程","NozzleRangeType",null,"MEnum","M","D2","1. 小射程（小于20m） 2. 中射程（20-40m） 3. 大射程（40以上） 99. 其他 (可多选)"]
[null,null,"喷头总个数","TotNozzleNum","个","Num","R","A2"]
[null,null,"最大喷灌流量","MaxSprayFlow","m3/h","Num","M","A2"]
[null,null,"喷头布置方式 ","NozzleLayoutType",null,"Enum","R","D1","1. 三角布置 2. 正方形布置 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"瞬时喷灌流量","SprayFlow","m3/h","Inst","M","L"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计喷灌水量","AccSprayWaterVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]
[]
[]
[null,null," "]

{"sheet":"WS水景系统","index":6,"n_rows":31,"n_cols":10,"rows_kept":31,"cut":false,"hidden":false,"merged":[[29,0,29,1],[30,0,30,1],[0,0,0,9],[1,0,1,1],[20,0,28,0],[2,1,5,1],[2,0,19,0],[11,1,19,1],[20,1,26,1],[27,1,28,1],[6,1,10,1]]}
["水景系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","整体","水景类型","WaterScapeType",null,"Enum","S","D1","1. 喷泉 2. 池塘 3. 人工瀑布 99. 其他"]
[null,null,"水源","WaterSourceType",null,"MEnum","S","D2","1. 雨水 2. 自来水 3. 中水 99. 其他（可多选）"]
[null,null,"水景总水量","DesignTotWaterVolume","m3","Num","M","A2"]
[null,null,"设计循环水量","DesignCycleWaterFlow","m3/h","Num","M","A2"]
[null,"喷泉","喷泉类型","SpringType",null,"Enum","S","D1","1. 普通喷泉 2. 壁泉 3. 旱泉 99. 其他"]
[null,null,"是否有电脑编程功能","isSpringProgramFunc",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"是否有灯光","isSpringLight",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"是否有音乐","isSpringMusic",null,"Bool","R","E1","0. 否 1. 是"]
[null,null,"喷头出水压力","SpringOutPress","MPa","Num","R","A2"]
[null,"园林","是否有菌床","isGardenFungiBed",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有浅石滩","isGardenReefFlat",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有底泥系统","isGardenSediment",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有瀑布","isGardenWaterfall",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"水生动物类型","GardenAquaticAnimalType",null,"MEnum","R","D2","1. 滤食性鱼类 2. 大型栖底无脊椎动物 99. 其他（可多选）"]
[null,null,"水生植物类型","GardenAquaticPlantType",null,"MEnum","R","D2","1. 荷花 2. 睡莲 3. 芦苇 4. 茭白 99. 其他（可多选）"]
[null,null,"是否机械循环","isGardenMachanicalPower",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"循环泵台数","GardenCyclePumpNum","台","Num","M","A2"]
[null,null,"循环泵出水压力","RatedGardenCyclePumpOutPress","MPa","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"系统循环水量","SysCycleWaterFlow","m3/h","Inst","M","L"]
[null,null,"系统总水量","SysTotWaterVolume","m3","Inst","M","L"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计循环水量","AccCycleWaterVolume ","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"WP泳池系统","index":7,"n_rows":33,"n_cols":10,"rows_kept":33,"cut":false,"hidden":false,"merged":[[0,0,0,9],[1,0,1,1],[2,0,16,0],[8,1,16,1],[2,1,7,1],[17,0,30,0],[17,1,27,1],[28,1,30,1],[31,0,31,1],[32,0,32,1]]}
["泳池系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数","整体","泳池类型","PoolType",null,"Enum","S","D1","1. 比赛泳池 2. 跳水泳池 3. 训练泳池 4. 戏水泳池 99. 其他"]
[null,null,"额定泳池水量","WaterCap","m3","Num","M","A2"]
[null,null,"额定泳池PH值","RatedWaterPH",null,"Num","S","A1"]
[null,null,"额定泳池水温","RatedWaterTemp","℃","Num","S","A2"]
[null,null,"过滤精度","FiltPrecision","μm","Num","M","A2"]
[null,null,"加热装置额定加热功率","RatedHeatP","kW","Num","M","A2"]
[null,"水处理","池水循环模式","CycleType",null,"Enum","M","D1","1. 顺流式 2. 逆流式 3. 混合式 99. 其他"]
[null,null,"循环泵台数","CyclePumpNum","台","Num","M","A2"]
[null,null,"循环泵出口压力","CyclePumpOutPress","MPa","Num","M","A2"]
[null,null,"额定循环水量","RatedCycleFlow","m3/h","Num","M","A2"]
[null,null,"是否有平衡水池","isBalanceBasin",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有紫外线装置","isUVEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有臭氧发生装置","isOzoneEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"是否有加药装置","isChemicalFeedEquip",null,"Bool","R","E1","0. 无 1. 有"]
[null,null,"加热方式","HeatType",null,"Enum","M","D1","1. 电加热 2. 盘管换热 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"泳池水量","WaterVolume","m3","Inst","M","L"]
[null,null,"泳池水温","WaterTemp","℃","Inst","S","L"]
[null,null,"泳池PH值","WaterPH",null,"Inst","M","L"]
[null,null,"补水量","FillingFlow","m3/h","Inst","R","L"]
[null,null,"循环水量","CycleFlow","m3/h","Inst","M","L"]
[null,null,"循环泵开启台数","CyclePumpRunNum","台","Inst","S","M"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计循环水量","AccCycleVolume","m3","Acc","M","M"]
[null,null,"累计补水量","AccFillingVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"FG燃气系统","index":8,"n_rows":20,"n_cols":10,"rows_kept":20,"cut":false,"hidden":false,"merged":[[18,0,18,1],[19,0,19,1],[0,0,0,9],[1,0,1,1],[10,0,17,0],[2,0,9,1],[10,1,16,1]]}
["燃气系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"系统形式","SysType",null,"Enum","M","D1","1. 一级 2. 二级 3. 三级 4. 多级 99. 其他","使用几级管网"]
[null,null,"管网形式","PipeNetType",null,"Enum","M","D1","1. 环状管网 2. 枝状管网 99. 其他"]
[null,null,"气源类型","GasType",null,"Enum","S","D1","1. 液化石油气 2. 天然气 3. 煤气 99. 其他"]
[null,null,"入户方式","UserConnectType",null,"Enum","M","D1","1. 水平式 2. 垂直式 99. 其他"]
[null,null,"用户类型","UserType",null,"Enum","S","D1","1. 居民用户 2. 公共建筑 3. 工业企业 99. 其他"]
[null,null,"设计供燃气量","DesignSupplyGasFlow","m3/h","Num","S","A2"]
[null,null,"设计供燃气户数","DesignSupplyGasUserNum","户","Num","M","A2"]
[null,null,"设计最不利末端燃气出口压力","RatedWorstTerminalOutPress","Pa","Num","M","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"瞬时用气量","GasConsumFlow","m3/h","Inst","M","L"]
[null,null,"瞬时用气户数","UserNum","户","Inst","R","L"]
[null,null,"最不利末端燃气出口压力","WorstTerminalOutPress","Pa","Inst","M","L"]
[null,"累计指标","累计用气量","AccGasConsumVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]

{"sheet":"WH给排水电伴热系统","index":9,"n_rows":20,"n_cols":10,"rows_kept":20,"cut":false,"hidden":false,"merged":[[18,0,18,1],[19,0,19,1],[0,0,0,9],[1,0,1,1],[2,0,7,1],[16,1,17,1],[8,0,17,0],[8,1,15,1]]}
["给排水电伴热系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"电伴热带类型","HeatTapeType",null,"Enum","M","D1","1. 基本型 2. C型 3. CT型 99. 其他"]
[null,null,"电伴热带额定功率","RatedP","kW","Num","S","A2"]
[null,null,"最低防冻温度","MinAntifreezeTemp","℃","Num","S","A2",null,"在此温度上依然能够防冻"]
[null,null,"最高表面温度","MaxSurfaceTemp","℃","Num","S","A2"]
[null,null,"设定维持温度","DesignHoldTemp","℃","Num","S","A2"]
[null,null,"安装方式","InstallType",null,"Enum","R","D1","1. 单线安装 2. 双线安装 99. 其他"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP",null,"Inst","M","M"]
[null,null,"平均暴露温度","AveExposureTemp",null,"Inst","R","M"]
[null,null,"平均表面温度","AveSurfaceTemp",null,"Inst","R","M"]
[null,null,"平均维持温度","AveHoldTemp",null,"Inst","R","M"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计加热量","AccHeat","kWh","Acc","R","M"]
["设定参数"]
["报警消息"]

{"sheet":"WD给排水人防系统","index":10,"n_rows":38,"n_cols":10,"rows_kept":38,"cut":false,"hidden":false,"merged":[[36,0,36,1],[37,0,37,1],[0,0,0,9],[1,0,1,1],[2,0,18,1],[19,0,35,0],[19,1,32,1],[33,1,35,1]]}
["给排水人防系统"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择","备注"]
["技术参数",null,"战时用途","WartimeFuncType",null,"Enum","S","D1","1. 指挥、通信 2. 中心医院及急救医院 3. 人员掩蔽部 4. 专业队装备部 5. 配套工程 99. 其他"]
[null,null,"人员等级","PersonLev",null,"Enum","S","D1","1. 专业队员 2. 一等人员（局级和局级以上） 3. 二等人员 99. 其他"]
[null,null,"抗力等级","ResistanceLev",null,"Enum","S","D1","1. 1级 2. 2级 3. 2b级 4. 3级 5. 4级 6. 4b级 7. 5级 8. 6级 99. 其他"]
[null,null,"防化等级","ChemicalDefenseLev",null,"Enum","S","D1","1. 甲级 2. 乙级 3. 丙级 4. 丁级 99. 其他"]
[null,null,"防护单元面积","RatedDefenseUnitArea","m2","Num","S","A2",null,"上限800m2"]
[null,null,"设计最大容量","DesignMaxPersonNum","人","Num","S","A2"]
[null,null,"一等人员饮用水标准","1stLevDrinkStandard","L/天","Num","R","A2"]
[null,null,"二等人员饮用水标准","2ndLevDrinkStandard","L/天","Num","R","A2"]
[null,null,"一等人员生活用水标准","1stLevDWStandard","L/天","Num","R","A2"]
[null,null,"二等人员生活用水标准","2ndLevDWStandard","L/天","Num","R","A2"]
[null,null,"墙、地面冲洗通水量","RatedFlushWaterVolume","L/m2","Num","R","A2"]
[null,null,"水箱容积","WaterTankCap","m3","Num","M","A2"]
[null,null,"集水坑容积","CollectBasinCap","m3","Num","M","A2"]
[null,null,"给水泵台数","SupplyPumpNum","台","Num","M","A2"]
[null,null,"污水泵台数","WastePumpNum","台","Num","M","A2"]
[null,null,"饮用水储水时间","DrinkWaterStoreTime","天","Num","R","A2"]
[null,null,"生活用水储水时间","DWStoreTime","天","Num","R","A2"]
["运行参数","瞬时状态","运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"本地远程状态","RemoteStatus",null,"Enumv","S","L","1. 本地 2. BA 3. 云端 99. 其他"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"系统耗电功率","SysElecConsumP","kW","Inst","M","M"]
[null,null,"防区专业队员人数","ProfessionalPersonNum","人","Inst","M","L"]
[null,null,"防区一等人员人数","1stLevPersonNum","人","Inst","M","L"]
[null,null,"防区二等人员人数","2ndLevPersonNum","人","Inst","M","L"]
[null,null,"饮用水供水量","DrinkSupplyFlow","m3/h","Inst","M","L"]
[null,null,"生活用水供水量","DWSupplyFlow","m3/h","Inst","M","L"]
[null,null,"水箱储水量","WaterTankVolume","m3","Inst","M","L"]
[null,null,"集水坑储水量","CollectBasinVolume","m3","Inst","M","L"]
[null,null,"给水泵开启台数","SupplyPumpRunNum","台","Inst","S","M"]
[null,null,"污水泵开启台数","WastePumpRunNum","台","Inst","S","M"]
[null,"累计指标","累计系统耗电量","AccSysElecConsum","kWh","Acc","M","M"]
[null,null,"累计饮用水供水量","AccDrinkSupplyVolume","m3","Acc","M","M"]
[null,null,"累计生活用水供水量","AccDWSupplyVolume","m3","Acc","M","M"]
["设定参数"]
["报警消息"]