{"text_format":"2","workbook":"xlsx","n_sheets":7,"sheets":["AEOV通断阀","AEAV调节阀","AECV止回阀","AERV减压阀","AESV安全阀","AERL继电器","AEFC变频器"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"AEOV通断阀","index":0,"n_rows":59,"n_cols":10,"rows_kept":59,"cut":false,"hidden":false,"merged":[[57,0,57,1],[58,0,58,1],[0,0,0,9],[41,1,50,1],[1,0,1,1],[51,0,56,1],[2,0,50,0],[2,1,40,1]]}
["通断阀"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","通用","电源类型","PowerType",null,"Enum","M","D1","1. 外接直流 2. 外接交流 3. 干电池 4. 充电电池 99. 其他"]
[null,null,"外接直流电压","ExDCU","V","Num","R","A2"]
[null,null,"外接交流电压","ExACU","V","Num","R","A2"]
[null,null,"干电池型号","DryCellType",null,"Enum","R","D1","1. AAAA 2. AAA 3. AA 4. A 5. SC 6. C 7. D 8. N 9. F 99. 其他"]
[null,null,"充电电压","RechargeU","V","Num","R","A2"]
[null,null,"是否有远程控制功能","isRemoteFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"是否有无线传输功能","isWirelessFunc",null,"Bool ","S","E1","0. 否 1. 是"]
[null,null,"有线协议","WireProtocol",null,"Enum","M","D1","1. RS-232 2. RS-485 3. CAN 4. TCP/IP 5. ADSL 6. FSK 7. 光纤 8. 电力载波 99. 其他"]
[null,null,"无线协议","WirelessProtocol",null,"MEnum","M","D2","1. Zigbee 2. RFID 3. 蓝牙技术 4. NFC 5. WiFi 99. 其他 （多选）"]
[null,null,"控制距离","CtrlDistance","m","Num","R","A2"]
[null,null,"操作方式","OperateType",null,"Enum","M","D1","1. 手动 2. 机械传动 3. 气动 4. 电动 5. 液动 99. 其他"]
[null,null,"通道类型","PortType",null,"Enum","R","D1","1. 直通式 2. 直角式 3. 三通式 4. 四通式 99. 其他"]
[null,null,"公称直径","Diameter","mm","Num","M","A2"]
[null,null,"公称压力","NominalPress","MPa","Num","R","A2"]
[null,null,"局部阻力系数","LocalResistanceCoeff",null,"Num","R","A1"]
[null,null,"适用介质","MediumType",null,"MEnum","S","D2","1. 空气 2. 燃气 3. 烟气（油烟） 4. 水 5. 蒸汽 6. 油品 7. 腐蚀介质 8. 放射性介质 9. 液态金属 99. 其他 （多选）"]
[null,null,"强度试验","StrengthTest","MPa","Num","R","A2"]
[null,null,"水密封试验","WaterSealTest","MPa","Num","R","A2"]
[null,null,"上密封试验","UpperSealTest","MPa","Num","R","A2"]
[null,null,"气密封试验","AirSealTest","MPa","Num","R","A2"]
[null,null,"阀体材料","BodyMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"阀芯材料","SpoolMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"连接方式","ConnectType",null,"Enum","R","D1","1. 法兰 2. 焊接 3. 内螺纹 4. 外螺纹 5. 对夹 99. 其他"]
[null,null,"法兰生产标准","FlangeStandard",null,"Str","R","B1"]
[null,null,"法兰尺寸n","FlangeN",null,"Num","R","A2"]
[null,null,"法兰尺寸d","FlangeD","mm","Num","R","A2"]
[null,null,"法兰距","FlangeDistance","mm","Num","R","A2"]
[null,null,"螺纹尺寸","ThreadSize","°","Num","R","A2"]
[null,null,"对夹螺栓孔中心直径","ClipBoltHoleDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓数量","ClipBoltNum","个","Num","R","A2"]
[null,null,"对夹螺栓直径","ClipBoltDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓长度","ClipBoltLength","mm","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"通断阀","阀分类","ValveType",null,"Enum","S","D1","1. 截止阀 2. 闸阀 3. 球阀 4. 蝶阀 5. 角座阀 99. 其他"]
[null,null,"控制形式","CtrlType",null,"Bool","R","E1","0. 单作用 1. 双作用"]
[null,null,"工作状态","WorkStatus",null,"Bool","M","E1","0. 常闭 1. 常开"]
[null,null,"截止阀分类","BreakValveType",null,"Enum","R","D1","1. 直通式截止阀 2. 直流式截止阀 3. 角式截止阀 4. 柱塞式截止阀 99. 其他","截止阀"]
[null,null,"闸阀阀杆种类","SluiceValveStemType",null,"Enum","R","D1","1. 明杆闸阀 2. 暗杆闸阀 99. 其他","闸阀"]
[null,null,"闸阀结构类型","SluiceValveStructureType",null,"Enum","R","D1","1. 平板闸阀 2. 楔式闸阀 99. 其他","闸阀"]
[null,null,"球阀结构类型","BallValveStructureType",null,"Enum","R","D1","1. 浮动求球阀 2. 固定球球阀 3. 弹性球球阀 99. 其他","球阀"]
[null,null,"蝶阀结构类型","ButterflyValveStructureType",null,"Enum","R","D1","1. 偏置板式 2. 垂直板式 3. 斜板式 4. 杠杆式 99. 其他","蝶阀"]
[null,null,"蝶阀密封结构形式","ButterflyValveSealType",null,"Enum","R","D1","1. 中心密封蝶阀 2. 单偏心密封蝶阀 3. 双偏心密封蝶阀 4. 三偏心密封蝶阀 99. 其他","蝶阀"]
[null,null,"角座阀执行器缸径","AngleSeatValveDiameter","mm","Num","R","A2",null,"角座阀"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"开闭状态","SwitchStatus",null,"Boolv","S","L","0. 关闭 1. 开启"]
["设定参数",null,"开闭设定","SwitchSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
["报警消息"]

{"sheet":"AEAV调节阀","index":1,"n_rows":70,"n_cols":10,"rows_kept":70,"cut":false,"hidden":false,"merged":[[67,0,68,1],[69,0,69,1],[0,0,0,9],[1,0,1,1],[41,1,59,1],[60,0,66,1],[2,0,59,0],[2,1,40,1]]}
["调节阀"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","通用","电源类型","PowerType",null,"Enum","M","D1","1. 外接直流 2. 外接交流 3. 干电池 4. 充电电池 99. 其他"]
[null,null,"外接直流电压","ExDCU","V","Num","R","A2"]
[null,null,"外接交流电压","ExACU","V","Num","R","A2"]
[null,null,"干电池型号","DryCellType",null,"Enum","R","D1","1. AAAA 2. AAA 3. AA 4. A 5. SC 6. C 7. D 8. N 9. F 99. 其他"]
[null,null,"充电电压","RechargeU","V","Num","R","A2"]
[null,null,"是否有远程控制功能","isRemoteFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"是否有无线传输功能","isWirelessFunc",null,"Bool ","S","E1","0. 否 1. 是"]
[null,null,"有线协议","WireProtocol",null,"Enum","M","D1","1. RS-232 2. RS-485 3. CAN 4. TCP/IP 5. ADSL 6. FSK 7. 光纤 8. 电力载波 99. 其他"]
[null,null,"无线协议","WirelessProtocol",null,"MEnum","M","D2","1. Zigbee 2. RFID 3. 蓝牙技术 4. NFC 5. WiFi 99. 其他 （多选）"]
[null,null,"控制距离","CtrlDistance","m","Num","R","A2"]
[null,null,"操作方式","OperateType",null,"Enum","M","D1","1. 手动 2. 机械传动 3. 气动 4. 电动 5. 液动 99. 其他"]
[null,null,"通道类型","PortType",null,"Enum","R","D1","1. 直通式 2. 直角式 3. 三通式 4. 四通式 99. 其他"]
[null,null,"公称直径","Diameter","mm","Num","M","A2"]
[null,null,"公称压力","NominalPress","MPa","Num","R","A2"]
[null,null,"局部阻力系数","LocalResistanceCoeff",null,"Num","R","A1"]
[null,null,"适用介质","MediumType",null,"MEnum","S","D2","1. 空气 2. 燃气 3. 烟气（油烟） 4. 水 5. 蒸汽 6. 油品 7. 腐蚀介质 8. 放射性介质 9. 液态金属 99. 其他 （多选）"]
[null,null,"强度试验","StrengthTest","MPa","Num","R","A2"]
[null,null,"水密封试验","WaterSealTest","MPa","Num","R","A2"]
[null,null,"上密封试验","UpperSealTest","MPa","Num","R","A2"]
[null,null,"气密封试验","AirSealTest","MPa","Num","R","A2"]
[null,null,"阀体材料","BodyMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"阀芯材料","SpoolMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"连接方式","ConnectType",null,"Enum","R","D1","1. 法兰 2. 焊接 3. 内螺纹 4. 外螺纹 5. 对夹 99. 其他"]
[null,null,"法兰生产标准","FlangeStandard",null,"Str","R","B1"]
[null,null,"法兰尺寸n","FlangeN",null,"Num","R","A2"]
[null,null,"法兰尺寸d","FlangeD","mm","Num","R","A2"]
[null,null,"法兰距","FlangeDistance","mm","Num","R","A2"]
[null,null,"螺纹尺寸","ThreadSize","°","Num","R","A2"]
[null,null,"对夹螺栓孔中心直径","ClipBoltHoleDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓数量","ClipBoltNum","个","Num","R","A2"]
[null,null,"对夹螺栓直径","ClipBoltDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓长度","ClipBoltLength","mm","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"调节阀","阀分类","ValveType",null,"Enum","M","D1","1. 调节阀 2. 平衡阀 99. 其他"]
[null,null,"阀行程种类","ValveTravelType",null,"Enum","R","D1","1. 直行程 2. 角行程 99. 其他"]
[null,null,"直行程阀种类","StraightTravelType",null,"Enum","R","D1","1. 单座阀 2. 双座阀 3. 套筒阀 4. 笼式阀 5. 角形阀 6. 三通阀 7. 隔膜阀 99. 其他"]
[null,null,"角行程阀种类","AngularTravelType",null,"Enum","R","D1","1. 蝶阀 2. 球阀 3. 偏心旋转阀 4. 全功能超轻型调节阀 99. 其他"]
[null,null,"上阀盖型式","BonnetType",null,"Enum","R","D1","1. 普通式（常温） 2. 热片式（中温） 3. 长颈式（低温） 99. 其他"]
[null,null,"流量特性类型","FlowCharacterType",null,"Enum","R","D1","1. 线性 2. 百分比 3. 快开 4. 抛物线 99. 其他"]
[null,null,"可调范围","AdjustRange",null,"Num","M","A1",null,"可调范围反映调节阀可控制的流量范围，用R＝Qmax：Qmin之比表示。R越大，调节流量的范围越宽，性能指标就越好。通常阀的R＝30，好的阀，如V型球阀、全功能超轻型调节阀，R可达100～200"]
[null,null,"允许泄漏量","AllowLeakage","%","Num","R","A2"]
[null,null,"基本误差","IntrinsicError","%","Num","R","A2"]
[null,null,"回差","Backlash","%","Num","R","A2"]
[null,null,"死区","DeadZone","%","Num","R","A2"]
[null,null,"始终点偏差","StartEndDeviation","%","Num","R","A2"]
[null,null,"额定行程偏差","RatedStrokeDeviation","%","Num","R","A2"]
[null,null,"执行机构推力","ActuatorThrust","N","Num","R","A2"]
[null,null,"执行机构允许最大压差","ActuatorMaxDetaPress","MPa","Num","R","A2"]
[null,null,"额定流量系数KV","RatedKV",null,"Num","R","A1"]
[null,null,"阀行程","ValveTravelLength","mm","Num","R","A2"]
[null,null,"平衡阀可调压差范围","BalanceValveDetaPressRange","Pa","Numr","M","A6",null,"平衡阀"]
[null,null,"平衡阀可调流量范围","BalanceValveDetaFlowRange","m3/h","Numr","M","A6",null,"平衡阀"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"开闭状态","SwitchStatus",null,"Boolv","S","L","0. 关闭 1. 开启"]
[null,null,"开度","Opening","%","Inst","S","L"]
["设定参数",null,"开闭设定","SwitchSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
[null,null,"开度设定","OpeningSet","%","Instp","S"]
["报警消息"]

{"sheet":"AECV止回阀","index":2,"n_rows":47,"n_cols":10,"rows_kept":47,"cut":false,"hidden":false,"merged":[[45,0,45,1],[46,0,46,1],[0,0,0,9],[1,0,1,1],[41,1,43,1],[2,0,43,0],[44,0,44,1],[2,1,40,1]]}
["止回阀"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","通用","电源类型","PowerType",null,"Enum","M","D1","1. 外接直流 2. 外接交流 3. 干电池 4. 充电电池 99. 其他"]
[null,null,"外接直流电压","ExDCU","V","Num","R","A2"]
[null,null,"外接交流电压","ExACU","V","Num","R","A2"]
[null,null,"干电池型号","DryCellType",null,"Enum","R","D1","1. AAAA 2. AAA 3. AA 4. A 5. SC 6. C 7. D 8. N 9. F 99. 其他"]
[null,null,"充电电压","RechargeU","V","Num","R","A2"]
[null,null,"是否有远程控制功能","isRemoteFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"是否有无线传输功能","isWirelessFunc",null,"Bool ","S","E1","0. 否 1. 是"]
[null,null,"有线协议","WireProtocol",null,"Enum","M","D1","1. RS-232 2. RS-485 3. CAN 4. TCP/IP 5. ADSL 6. FSK 7. 光纤 8. 电力载波 99. 其他"]
[null,null,"无线协议","WirelessProtocol",null,"MEnum","M","D2","1. Zigbee 2. RFID 3. 蓝牙技术 4. NFC 5. WiFi 99. 其他 （多选）"]
[null,null,"控制距离","CtrlDistance","m","Num","R","A2"]
[null,null,"操作方式","OperateType",null,"Enum","M","D1","1. 手动 2. 机械传动 3. 气动 4. 电动 5. 液动 99. 其他"]
[null,null,"通道类型","PortType",null,"Enum","R","D1","1. 直通式 2. 直角式 3. 三通式 4. 四通式 99. 其他"]
[null,null,"公称直径","Diameter","mm","Num","M","A2"]
[null,null,"公称压力","NominalPress","MPa","Num","R","A2"]
[null,null,"局部阻力系数","LocalResistanceCoeff",null,"Num","R","A1"]
[null,null,"适用介质","MediumType",null,"MEnum","S","D2","1. 空气 2. 燃气 3. 烟气（油烟） 4. 水 5. 蒸汽 6. 油品 7. 腐蚀介质 8. 放射性介质 9. 液态金属 99. 其他 （多选）"]
[null,null,"强度试验","StrengthTest","MPa","Num","R","A2"]
[null,null,"水密封试验","WaterSealTest","MPa","Num","R","A2"]
[null,null,"上密封试验","UpperSealTest","MPa","Num","R","A2"]
[null,null,"气密封试验","AirSealTest","MPa","Num","R","A2"]
[null,null,"阀体材料","BodyMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"阀芯材料","SpoolMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"连接方式","ConnectType",null,"Enum","R","D1","1. 法兰 2. 焊接 3. 内螺纹 4. 外螺纹 5. 对夹 99. 其他"]
[null,null,"法兰生产标准","FlangeStandard",null,"Str","R","B1"]
[null,null,"法兰尺寸n","FlangeN",null,"Num","R","A2"]
[null,null,"法兰尺寸d","FlangeD","mm","Num","R","A2"]
[null,null,"法兰距","FlangeDistance","mm","Num","R","A2"]
[null,null,"螺纹尺寸","ThreadSize","°","Num","R","A2"]
[null,null,"对夹螺栓孔中心直径","ClipBoltHoleDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓数量","ClipBoltNum","个","Num","R","A2"]
[null,null,"对夹螺栓直径","ClipBoltDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓长度","ClipBoltLength","mm","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"止回阀","阀分类","ValveType",null,"Enum","M","D1","1. 升降式止回阀 2. 旋启式止回阀 3. 蝶式止回阀 4. 底阀 99. 其他"]
[null,null,"升降式分类","LiftType",null,"Enum","R","D1","1. 直通流道 2. 立式结构 3. 角式流道 99. 其他","升降式"]
[null,null,"旋启式分类","SwingType",null,"Enum","R","D1","1. 单瓣 2. 双瓣 3. 多瓣 99. 其他","旋启式"]
["运行参数"]
["设定参数"]
["报警消息"]

{"sheet":"AERV减压阀","index":3,"n_rows":52,"n_cols":10,"rows_kept":52,"cut":false,"hidden":false,"merged":[[49,0,49,1],[50,0,50,1],[51,0,51,1],[0,0,0,9],[1,0,1,1],[41,1,48,1],[2,0,48,0],[2,1,40,1]]}
["减压阀"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","通用","电源类型","PowerType",null,"Enum","M","D1","1. 外接直流 2. 外接交流 3. 干电池 4. 充电电池 99. 其他"]
[null,null,"外接直流电压","ExDCU","V","Num","R","A2"]
[null,null,"外接交流电压","ExACU","V","Num","R","A2"]
[null,null,"干电池型号","DryCellType",null,"Enum","R","D1","1. AAAA 2. AAA 3. AA 4. A 5. SC 6. C 7. D 8. N 9. F 99. 其他"]
[null,null,"充电电压","RechargeU","V","Num","R","A2"]
[null,null,"是否有远程控制功能","isRemoteFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"是否有无线传输功能","isWirelessFunc",null,"Bool ","S","E1","0. 否 1. 是"]
[null,null,"有线协议","WireProtocol",null,"Enum","M","D1","1. RS-232 2. RS-485 3. CAN 4. TCP/IP 5. ADSL 6. FSK 7. 光纤 8. 电力载波 99. 其他"]
[null,null,"无线协议","WirelessProtocol",null,"MEnum","M","D2","1. Zigbee 2. RFID 3. 蓝牙技术 4. NFC 5. WiFi 99. 其他 （多选）"]
[null,null,"控制距离","CtrlDistance","m","Num","R","A2"]
[null,null,"操作方式","OperateType",null,"Enum","M","D1","1. 手动 2. 机械传动 3. 气动 4. 电动 5. 液动 99. 其他"]
[null,null,"通道类型","PortType",null,"Enum","R","D1","1. 直通式 2. 直角式 3. 三通式 4. 四通式 99. 其他"]
[null,null,"公称直径","Diameter","mm","Num","M","A2"]
[null,null,"公称压力","NominalPress","MPa","Num","R","A2"]
[null,null,"局部阻力系数","LocalResistanceCoeff",null,"Num","R","A1"]
[null,null,"适用介质","MediumType",null,"MEnum","S","D2","1. 空气 2. 燃气 3. 烟气（油烟） 4. 水 5. 蒸汽 6. 油品 7. 腐蚀介质 8. 放射性介质 9. 液态金属 99. 其他 （多选）"]
[null,null,"强度试验","StrengthTest","MPa","Num","R","A2"]
[null,null,"水密封试验","WaterSealTest","MPa","Num","R","A2"]
[null,null,"上密封试验","UpperSealTest","MPa","Num","R","A2"]
[null,null,"气密封试验","AirSealTest","MPa","Num","R","A2"]
[null,null,"阀体材料","BodyMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"阀芯材料","SpoolMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"连接方式","ConnectType",null,"Enum","R","D1","1. 法兰 2. 焊接 3. 内螺纹 4. 外螺纹 5. 对夹 99. 其他"]
[null,null,"法兰生产标准","FlangeStandard",null,"Str","R","B1"]
[null,null,"法兰尺寸n","FlangeN",null,"Num","R","A2"]
[null,null,"法兰尺寸d","FlangeD","mm","Num","R","A2"]
[null,null,"法兰距","FlangeDistance","mm","Num","R","A2"]
[null,null,"螺纹尺寸","ThreadSize","°","Num","R","A2"]
[null,null,"对夹螺栓孔中心直径","ClipBoltHoleDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓数量","ClipBoltNum","个","Num","R","A2"]
[null,null,"对夹螺栓直径","ClipBoltDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓长度","ClipBoltLength","mm","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"减压阀","阀分类","ValveType",null,"Enum","M","D1","1. 组合式 2. 作用式 3. 活塞式 4. 薄膜式 99. 其他"]
[null,null,"额定CV值","RatedCV",null,"Num","R","A1"]
[null,null,"最高进口压力","MaxInPress","Pa","Num","M","A2"]
[null,null,"出口压力范围","OutPressRange","Pa","Numr","M","A2"]
[null,null,"压力特性偏差","PressCharDeta","%","Num","R","A2",null,"GB12246-1989"]
[null,null,"流量特性偏差","FlowCharDeta","%","Num","R","A2",null,"GB12246-1989"]
[null,null,"最小压差","MinDetaPress","Pa","Num","R","A2"]
[null,null,"渗漏量","Leakage","%","Num","R","A2"]
["运行参数"]
["设定参数"]
["报警消息"]

{"sheet":"AESV安全阀","index":4,"n_rows":71,"n_cols":10,"rows_kept":71,"cut":false,"hidden":false,"merged":[[69,0,69,1],[70,0,70,1],[0,0,0,9],[1,0,1,1],[63,0,68,1],[2,1,40,1],[41,1,62,1],[2,0,62,0]]}
["安全阀"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","通用","电源类型","PowerType",null,"Enum","M","D1","1. 外接直流 2. 外接交流 3. 干电池 4. 充电电池 99. 其他"]
[null,null,"外接直流电压","ExDCU","V","Num","R","A2"]
[null,null,"外接交流电压","ExACU","V","Num","R","A2"]
[null,null,"干电池型号","DryCellType",null,"Enum","R","D1","1. AAAA 2. AAA 3. AA 4. A 5. SC 6. C 7. D 8. N 9. F 99. 其他"]
[null,null,"充电电压","RechargeU","V","Num","R","A2"]
[null,null,"是否有远程控制功能","isRemoteFunc",null,"Bool","S","E1","0. 否 1. 是"]
[null,null,"是否有无线传输功能","isWirelessFunc",null,"Bool ","S","E1","0. 否 1. 是"]
[null,null,"有线协议","WireProtocol",null,"Enum","M","D1","1. RS-232 2. RS-485 3. CAN 4. TCP/IP 5. ADSL 6. FSK 7. 光纤 8. 电力载波 99. 其他"]
[null,null,"无线协议","WirelessProtocol",null,"MEnum","M","D2","1. Zigbee 2. RFID 3. 蓝牙技术 4. NFC 5. WiFi 99. 其他 （多选）"]
[null,null,"控制距离","CtrlDistance","m","Num","R","A2"]
[null,null,"操作方式","OperateType",null,"Enum","M","D1","1. 手动 2. 机械传动 3. 气动 4. 电动 5. 液动 99. 其他"]
[null,null,"通道类型","PortType",null,"Enum","R","D1","1. 直通式 2. 直角式 3. 三通式 4. 四通式 99. 其他"]
[null,null,"公称直径","Diameter","mm","Num","M","A2"]
[null,null,"公称压力","NominalPress","MPa","Num","R","A2"]
[null,null,"局部阻力系数","LocalResistanceCoeff",null,"Num","R","A1"]
[null,null,"适用介质","MediumType",null,"MEnum","S","D2","1. 空气 2. 燃气 3. 烟气（油烟） 4. 水 5. 蒸汽 6. 油品 7. 腐蚀介质 8. 放射性介质 9. 液态金属 99. 其他 （多选）"]
[null,null,"强度试验","StrengthTest","MPa","Num","R","A2"]
[null,null,"水密封试验","WaterSealTest","MPa","Num","R","A2"]
[null,null,"上密封试验","UpperSealTest","MPa","Num","R","A2"]
[null,null,"气密封试验","AirSealTest","MPa","Num","R","A2"]
[null,null,"阀体材料","BodyMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"阀芯材料","SpoolMaterial",null,"Enum","R","D1","1. 碳钢 2. 铸铁 3. 合金钢 4. 铜合金 5. 铝合金 6. 铅合金 7. 钛合金 8. 塑料 9. 陶瓷 10. 玻璃钢 99. 其他"]
[null,null,"连接方式","ConnectType",null,"Enum","R","D1","1. 法兰 2. 焊接 3. 内螺纹 4. 外螺纹 5. 对夹 99. 其他"]
[null,null,"法兰生产标准","FlangeStandard",null,"Str","R","B1"]
[null,null,"法兰尺寸n","FlangeN",null,"Num","R","A2"]
[null,null,"法兰尺寸d","FlangeD","mm","Num","R","A2"]
[null,null,"法兰距","FlangeDistance","mm","Num","R","A2"]
[null,null,"螺纹尺寸","ThreadSize","°","Num","R","A2"]
[null,null,"对夹螺栓孔中心直径","ClipBoltHoleDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓数量","ClipBoltNum","个","Num","R","A2"]
[null,null,"对夹螺栓直径","ClipBoltDiameter","mm","Num","R","A2"]
[null,null,"对夹螺栓长度","ClipBoltLength","mm","Num","R","A2"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"压力等级","PressLev",null,"Enum","M","D1","1. 低压L 2. 中压M 3. 高压H 4. 超高压U 99. 其他"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,null,"介质温度范围","MediumTempRange","℃","Numr","R","A6"]
[null,null,"理论压力损失","RatedPressLost","Pa","Num","R","A2"]
[null,"安全阀","阀分类","ValveType",null,"Enum","S","D1","1. 疏水阀 2. 防火阀 3. 排烟阀 4. 排气阀 99. 其他"]
[null,null,"加载机构分类","MechanismType",null,"Enum","R","D1","1. 重锤杠杆式 2. 弹簧式 3. 脉冲式 99. 其他"]
[null,null,"排放方式分类","DischargeType",null,"Enum","R","D1","1. 全封闭式 2. 半封闭式 3. 开放式 99. 其他"]
[null,null,"作用方式","ActionType",null,"Bool","R","E1","0. 直接作用 1. 间接作用"]
[null,null,"是否可调","isAdjust",null,"Bool","M","E1","0. 否 1. 是"]
[null,null,"开启压力","OpenPress","Pa","Num","M","A2",null,"整定压力，是安全阀阀瓣在运行条件下开始升起时的介质压力"]
[null,null,"结构尺寸","StructureSize","mm","Num","R","A2"]
[null,null,"壳体强度","ShellStrength","Pa","Num","R","A2",null,"壳体在外力作用下抵抗破坏（变形和断裂）的能力称为强度"]
[null,null,"疏水阀结构形式","TrapValveType",null,"Enum","R","D1","1. 机械型 2. 热静力型 3. 热动力型 99. 其他","疏水阀"]
[null,null,"疏水阀无负荷漏汽率","TrapValveNoLoadLeakageRate","%","Num","R","A2",null,"疏水阀"]
[null,null,"疏水阀过冷度","TrapValveUndercool","℃","Num","R","A2",null,"疏水阀"]
[null,null,"疏水阀最高背压率","TrapValveMaxBackPressRate","℃","Num","R","A2",null,"疏水阀"]
[null,null,"排气阀类型","ReliefValveType",null,"Enum","R","D1","1. 暖气式 2. 微量式 3. 快速式 4. 复合式 99. 其他","排气阀"]
[null,null,"排气阀水关闭压力","ReliefValveWaterOffPress","Pa","Num","R","A2",null,"排气阀"]
[null,null,"排气阀空气关闭压力","ReliefValveAirOffPress","Pa","Num","R","A2",null,"排气阀"]
[null,null,"防火阀熔断关闭温度","FireValveFuseOffTemp","℃","Num","R","A2",null,"防火阀"]
[null,null,"防火阀转动力矩","FireValveRotateTorque","Nm","Num","R","A2",null,"防火阀"]
[null,null,"排烟阀开启温度","SmokeValveOpenTemp","℃","Num","R","A2",null,"排烟阀"]
[null,null,"排烟阀熔断关闭温度","SmokeValveFuseOffTemp","℃","Num","R","A2",null,"排烟阀"]
[null,null,"排烟阀转动力矩","SmokeValveRotateTorque","Nm","Num","R","A2",null,"排烟阀"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"阻燃等级","FlameRetardantLev",null,"Enum","M","D1","1. HB 2. V-2 3. V-1 4. V-0 99. 其他"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"开闭状态","SwitchStatus",null,"Boolv","S","L","0. 关闭 1. 开启"]
["设定参数",null,"开闭设定","SwitchSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
["报警消息"]

{"sheet":"AERL继电器","index":5,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[[42,0,42,1],[43,0,43,1],[0,0,0,9],[1,0,1,1],[18,1,25,1],[26,1,34,1],[35,0,41,1],[2,0,34,0],[2,1,17,1]]}
["继电器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数","整体","防护特征","ProtectType",null,"Enum","R","D1","1. 密封式 2. 封闭式 3. 敞开式 99. 其他","密封：采用焊接或其它方法，将触点和线圈等都密封在罩壳内，与周围介质相隔离，泄漏率较低的继电器；封闭：将触点和线圈等都封闭（非密封）在罩壳内加以防护的继电器；敞开：不用防护罩来保护触点和线圈等的继电器"]
[null,null,"工作状态","WorkStatus",null,"Bool","S","E1","0. 常断 1. 常通"]
[null,null,"响应时间","ResponseTime","ms","Num","M","A2"]
[null,null,"复位时间","ResetTime","ms","Num","M","A2"]
[null,null,"动作电压","OperateU","V","Num","R","A2"]
[null,null,"复位电压","ResetU","V","Num","R","A2"]
[null,null,"最大机械开关频率","MaxMechanicalSwitchFreq","次/h","Num","R","A2"]
[null,null,"最大额定负载开关频率","MaxLoadSwitchFreq","次/h","Num","R","A2"]
[null,null,"绝缘电阻","InsulationResistance","Ω","Num","M","A2"]
[null,null,"误动作","Maloperation","m/s2","Num","R","A2",null,"在多大加速度下会产生错误闭和或开启"]
[null,null,"机械寿命","MechanicalLife","次","Num","R","A2",null,"机械寿命为空载下的未失效开关次数，通过弹性机构衡量是否失效"]
[null,null,"电气寿命","ElectricalLife","次","Num","R","A2",null,"电气寿命为额定实验条件下的未失效开关次数，通过测量触点电阻或者触电损坏衡量是否失效"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"工作温度范围","WorkTempRange","℃","Numr","M","A6"]
[null,null,"工作湿度范围","WorkRHRange","%RH","Numr","M","A6"]
[null,null,"平均无故障时间","MTBF","h","Num","M","A2"]
[null,"线圈","线圈额定电流","CoilRateI","A","Num","R","A2"]
[null,null,"线圈额定电压","CoilRateU","V","Num","R","A2"]
[null,null,"线圈电阻","CoilResistance","Ω","Num","R","A2"]
[null,null,"线圈最大连续容许电压","CoilMaxAllowU","V","Num","R","A2"]
[null,null,"线圈最大吸合电压","CoilMaxConnectU","V","Num","R","A2"]
[null,null,"线圈最小释放电压","CoilMiniReleaseU","V","Num","R","A2"]
[null,null,"线圈最大过载电压","CoilMaxOverloadU","V","Num","R","A2"]
[null,null,"线圈功耗","CoilRatedP","W","Num","R","A2"]
[null,"触点","触点材料","ContactorMaterial",null,"Enum","R","D1","1. 纯金属 2. 金属合金 3. 金属陶瓷 99. 其他"]
[null,null,"触点额定直流电压","ContactorRateDCU","V","Num","R","A2"]
[null,null,"触点额定直流电流","ContactorRateDCI","A","Num","R","A2"]
[null,null,"触点额定交流电压","ContactorRateACU","V","Num","R","A2"]
[null,null,"触点额定交流电流","ContactorRateACI","A","Num","R","A2"]
[null,null,"触点最大转换电压","ContactorMaxConverseU","V","Num","R","A2"]
[null,null,"触点最大转换电流","ContactorMaxConverseI","A","Num","R","A2"]
[null,null,"触点最大转换功率","ContactorMaxConverseP","W","Num","R","A2"]
[null,null,"触点接触电阻","ContactorResistance","Ω","Num","R","A2"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"开合状态","SwitchStatus",null,"Boolv","S","L","0. 断开 1. 闭合"]
[null,null,"通过电流","I","A","Inst","R","L"]
["设定参数",null,"开合设定","SwitchSet",null,"Boolp","S",null,"0. 断开 1. 闭合"]
["报警消息"]

{"sheet":"AEFC变频器","index":6,"n_rows":42,"n_cols":10,"rows_kept":42,"cut":false,"hidden":false,"merged":[[39,0,40,1],[41,0,41,1],[0,0,0,9],[1,0,1,1],[31,0,38,1],[2,0,30,1]]}
["变频器"]
["分级标签",null,"信息点","信息点编码","单位","类型","优先级","输入方式","字典选择"," 备注"]
["技术参数",null,"输入电压等级","InUType",null,"Enum","M","D1","1. 低压变频器 2. 中压变频器 3. 高压变频器 99. 其他"]
[null,null,"输入相数","InPhaseType",null,"MEnum","R","D2","1. 单相 2. 三相 99. 其他 （多选） "]
[null,null,"输入电压上限","InUUpperLimit","V","Num","R","A2"]
[null,null,"输入电压下限","InULowerLimit","V","Num","R","A2"]
[null,null,"输入额定电流","InRateI","A","Num","R","A2"]
[null,null,"输入频率上限","InFreqUpperLimit","Hz","Num","R","A2"]
[null,null,"输入频率下限","InFreqLowerLimit","Hz","Num","R","A2"]
[null,null,"电网类型","PowerGridType",null,"Enum","R","D1","1. TT 2. TNC 3. TNS 4. IT 99. 其他"]
[null,null,"功率因数","PFactor",null,"Num","R","A1"]
[null,null,"效率","Eff","%","Num","R","A2"]
[null,null,"过载能力","OverloadCap",null,"Str","M","B1",null,"eg：150%额定负载电流持续时间60s；工作周期时间300s"]
[null,null,"过压等级","OverpressLev",null,"Enum","M","D1","1. Ⅰ 2. Ⅱ 3. Ⅲ 4. Ⅳ 99. 其他","IEC61800-5-1"]
[null,null,"噪音等级","Noise","dB(A)","Num","R","A2",null,"发出的噪音强度上限"]
[null,null,"输出频率上限","OutFreqUpperLimit","Hz","Num","S","A2"]
[null,null,"输出频率下限","OutFreqLowerLimit","Hz","Num","S","A2"]
[null,null,"开关频率","RateSwitchFreq","kHz","Num","R","A2",null,"通过调节开关频率，可以实现系统的噪音最小，波形的平滑型最好，同时干扰也是最小。 因为变频器大多是采用PWM调制的形式进行变频器的。也就是说变频器输出的电压其实是一系列的脉冲，脉冲的宽度和间隔均不相等。其大小就取决于调制波和载波的交点，也就是开关频率。开关频率越高，一个周期内脉冲的个数就越多，电流波形的平滑性就越好，但是对其它设备的干扰也越大。载波频率越低或者设置的不好，电机就会发出难听的噪音。同时调整变频器的开关频率，可调整功率损耗 。因为功率模块IGBT的功率损耗与变频器的开关频率有关，且随变频器的开关频率的提高、功率损耗增大，这样一则使效率下降，二则是功率模块发热增加，对运行是不利的，当然变频器的工作电压越高，影响功率损耗亦加大"]
[null,null,"对应开关频率下的最大持续输出电流","MaxContinueOutI","A","Num","R","A2",null,"与开关频率长度相同的向量一一对应"]
[null,null,"冷却方法","CoolType",null,"Enum","R","D1","1. 自然冷却 2. 强制风冷 99. 其他"]
[null,null,"防护等级","IPGrade",null,"Str","S","B1","参考《11防护等级》"]
[null,null,"绝缘等级","InsulationLev",null,"Enum","M","D1","1. Y级 2. A级 3. E级 4. B级 5. F级 6. H级 7. C级 8. N级 9. R级 99. 其他"]
[null,null,"防爆等级","ExplosionProofLev",null,"Enum","M","D1","1. I类 2. II类 2.1 IIA类 2.2 IIB类 2.3 IIC类 3. III类 3.1 IIIA类 3.2 IIIB类 3.3 IIIC类 99. 其他"]
[null,null,"无降容运行温度范围","NoReduceCapWorkTempRange","℃","Numr","M","A6"]
[null,null,"降容运行温度范围","ReduceCapWorkTempRange","℃","Numr","M","A6"]
[null,null,"无降容运行海拔高度范围","NoReduceCapWorkElevationRange","m","Numr","R","A6"]
[null,null,"降容运行海拔高度范围","ReduceCapWorkElevationRange","m","Numr","R","A6"]
[null,null,"工作湿度范围","WorkRHRange","%","Numr","R","A6"]
[null,null,"是否有高海拔要求","isHighAltitude",null,"Bool","R","E1","0. 无高海拔设计 1. 高海拔专用（＞1000米）"]
[null,null,"是否有防盐雾要求","isSaltFogDefend",null,"Bool","R","E1","0. 无防盐雾设计 1. 沿海地区专用"]
[null,null,"能效等级","EEffIndex",null,"Enum","M","D1","1. 1级 2. 2级 3. 3级 4. 4级 5. 5级 99. 其他"]
["运行参数",null,"运行状态","RunStatus",null,"Boolv","S","L","0. 停止 1. 运行"]
[null,null,"故障状态","FaultStatus",null,"Boolv","S","L","0. 正常 1. 故障"]
[null,null,"手自动状态","ManualAutoStatus",null,"Boolv","S","L","0. 手动 1. 自动"]
[null,null,"云端控制状态","InCloudStatus",null,"Boolv","S","L","0. 非云端 1. 云端"]
[null,null,"BA手动干预状态","BAInterveneStatus",null,"Boolv","S","L","0. 不允许 1. 允许"]
[null,null,"输出电流","OutI","A","Inst","M","L"]
[null,null,"输入频率","InFreq","Hz","Inst","S","L"]
[null,null,"输出频率","OutFreq","Hz","Inst","S","L"]
["设定参数",null,"运行状态设定","RunSet",null,"Boolp","S",null,"0. 关闭 1. 开启"]
[null,null,"输出频率设定","OutFreqSet","Hz","Instp","S"]
["故障报警"]