{"text_format":"2","workbook":"xlsx","n_sheets":18,"sheets":["检查结果汇总","楼层平面图命名规范检查","构件范围检查","项目长度单位检查","设备族编码检查","部件所在位置检查","柱边界检查","连接件检查","系统类型名称检查","未在空间中的设备","管段检查","管网及相关设备检查","Revit族参数完整性检查","xyz坐标重叠检查","参考-revit分类","参考-连接件对照表","参考-可识别的系统名称","参考-管网及相关设备"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":14,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"检查结果汇总","index":0,"n_rows":1,"n_cols":3,"rows_kept":1,"cut":false,"hidden":false,"merged":[]}
["全部检查项","是否选择进行检查","结果"]

{"sheet":"楼层平面图命名规范检查","index":1,"n_rows":5,"n_cols":3,"rows_kept":5,"cut":false,"hidden":false,"merged":[[1,0,2,0],[0,1,0,2],[1,1,1,2],[2,1,2,2]]}
["检查内容","1.模型中有且仅有一个-saga后缀的楼层平面视图\n2.带saga标记的楼层平面视图编码符合建模规范要求\n3.是否缺少RF标高，saga平面所在标高应不大于RF标高"]
["方法","1.不通过时，不再进行2检查\n1、2未全部通过时不再进行后续检查项（楼层平面图命名规范检查通过为所有检查项的前置条件）"]
[null,"1.标注saga,是标注楼层平面视图，其它类型的视图也可以标记，检查时只检查楼层平面。\n获取所有的楼层--检查并保存楼层平面视图\n2.打标记的楼层名称必需为指定格式；B1,B1M,F1,F1M1,F1M2,RFM,RFM1,RF\n^([BF][1-9]\\d*M?\\d?|RFM?\\d?)-saga$\n3.检查RF标高是否存在，RF标高与当前层标高对比。"]
[]
["楼层平面视图名称","通过","备注（失败原因）"]

{"sheet":"构件范围检查","index":2,"n_rows":5,"n_cols":5,"rows_kept":5,"cut":false,"hidden":false,"merged":[[1,0,2,0],[0,1,0,4],[1,1,1,4],[2,1,2,4],[3,0,3,4]]}
["检查内容","1，正常情况下构件应该位于当前层和上一层之间；\n2，如果上一层为夹层，构件可位于当前层和夹层的上一层之前；\n3，如果当前层是屋顶或屋顶夹层，构件应该位置当前层之上，顶部不约束。"]
["方法","当前层绝对高度Hb,上一层为夹层时绝对高度为Hj，上一层绝对高度Ht，如果上一层不是夹层Hj=Ht;\n冗余为W=500;\n如果是屋顶，顶部范围为正无穷"]
[null,"墙底部高度Zb,顶部为Zt\n判定规则：\nZb∈[Hb-W,Hb]\nZt∈[Hj-W,Hj]∪[Ht-W,Ht]"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","类型（设备、部件、信标、墙、柱、空间）","ID","通过","备注（失败原因）"]

{"sheet":"项目长度单位检查","index":3,"n_rows":4,"n_cols":2,"rows_kept":4,"cut":false,"hidden":false,"merged":[]}
["检查内容","项目长度单位是否为毫米（mm）"]
["方法","获取Document的单位系统，判断长度的单位是否为毫米（mm）"]
[]
["通过","备注（失败原因）"]

{"sheet":"设备族编码检查","index":4,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[0,1,0,3],[1,1,1,3],[2,0,2,3]]}
["检查内容","指定的Revit分类（Category）下的所有对象，族名称应该按照数据字典规定格式进行编码（详见sheet页：参考-revit分类）"]
["方法","1，获取需要检查的Reivt分类（Category），例如：机械设备，常规模型；\n2，从模型中获取每个分类下的所有对象；\n3，按分类族名称进行分组；\n4，依次检查分组后的族名称，是否为可识别类型。\n注：设备四位编码；部件六位编码；信标Beacon"]
[]
["族名称","类型","通过","备注（失败原因）"]

{"sheet":"部件所在位置检查","index":5,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[1,1,1,3],[0,1,0,3]]}
["检查内容","部件是否有依赖的设备（数据字典规定，部件必须依赖一个设备）"]
["方法","1，获取与部件相交的所有实体；\n2，过滤出与部件编码前四位相同的实体。\n注：部件编码的前四位与其依赖的设备编码相同，\n例：设备：TDLS低压开关柜；部件：TDLSDW低压配电抽屉。"]
[]
["族名称","ID","通过","备注（失败原因）"]

{"sheet":"柱边界检查","index":6,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[0,1,0,3],[1,1,1,3],[2,0,2,3]]}
["检查内容","结构柱是否为模型边界（影响空间范围），建模要求是结构柱，墙为建筑墙"]
["方法","柱的房间边界参数是否选中"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","ID","通过","备注（失败原因）"]

{"sheet":"连接件检查","index":7,"n_rows":4,"n_cols":5,"rows_kept":4,"cut":false,"hidden":false,"merged":[[0,1,0,4],[1,1,1,4],[2,0,2,4]]}
["检查内容","1.判断设备是否有连接件（连接件类型：限定水管和风管）;\n2.有连接件的设备是否都已经连接上\n（详见sheet页：参考-连接件对照表）"]
["方法","1.1，读取连接件对照表数据；\n1.2，获取所有的设备或部件；\n1.3，遍历每个构件， 从连接件表中取设备类是否有风和水连接件；判断连接件是否存在。\n2.1，1.通过时，判断连接件连接状态，是否已连接。IsConnector==True\n注：1.不通过时，不再进行2检查"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","类型（设备）","ID","通过","备注（失败原因）"]

{"sheet":"系统类型名称检查","index":8,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[1,1,1,3],[0,1,0,3]]}
["检查内容","模型中系统类型名称与物理世界可识别的拓扑图名称是否一致（详见sheet页：参考-可识别的系统名称）"]
["方法","1，获取可识别系统名称列表；\n2，过滤出模型中的风管系统和管道系统；\n3，遍历系统类型与给定系统鏊列表比对判断系统名称是否可识别。"]
[]
["系统名称","系统类型（风管系统，管道系统）","通过","备注（失败原因）"]

{"sheet":"未在空间中的设备","index":9,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[1,1,1,3],[0,1,0,3],[2,0,2,3]]}
["检查内容","原则上设备和部件都应该在空间中，导出没有空间中的设备，部件"]
["方法","1，获取本楼层所有设备和部件；\n2，逐个检查每个设备或部件，判断是否在空间中。"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","ID","通过","备注（失败原因）"]

{"sheet":"管段检查","index":10,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[2,0,2,3],[0,1,0,3],[1,1,1,3]]}
["检查内容","检查管段两端是否都已经连接；检查管段连接的临近管段系统类型是否一致"]
["方法","前置条件：\n指定检查的管道（水管和风管）系统类型名称\n获取本层此 系统类型名称 的管段\n1、检查管段。管道有断开的Conector\n获取管段的所有Connector\n检查是否有未连接的Connector,否标记:001\nstart立管特殊，允许有未连接的Connector；\n2、检查管段。连接两端管段（注意不是弯头）系统类型名称与本管段系统类型名称相同\n获取本管段的连接管段或设备\n检查连接管段的系统类型名称和本管段的系统类型名称是否相同；否标记：002\n设备忽略\n"]
["共检查XXX条数据，未通过检查的如下"]
["管道类型","ID","通过","备注（失败原因）"]

{"sheet":"管网及相关设备检查","index":11,"n_rows":4,"n_cols":6,"rows_kept":4,"cut":false,"hidden":false,"merged":[[0,1,0,5],[1,1,1,5],[2,0,2,5]]}
["检查内容"," 检查设备连接的管道系统是否与规范一致。规范（详见sheet页：参考-管网及相关设备）   "]
["方法","1，获取本层所有的设备和部件；\n2，获取 参考规范中设备与系统的对应关系；\n3，遍历设备所有的连接件，判断连接件所连接的管道系统与规范是否一致。"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","ID","通过检查的管网连接","未通过检查的管网连接","通过","备注（失败原因）"]

{"sheet":"Revit族参数完整性检查","index":12,"n_rows":4,"n_cols":3,"rows_kept":4,"cut":false,"hidden":false,"merged":[[2,0,2,2],[0,1,0,2],[1,1,1,2]]}
["检查内容","检查设备族参数“设备本地名称”、“设备本地编码”是否缺失"]
["方法","1，获取本层所有的设备和部件；\n2，按族名称进行分组；\n3，遍历分组，检查参数“设备本地名称”、“设备本地编码”是否存在。"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","通过","备注（失败原因）"]

{"sheet":"xyz坐标重叠检查","index":13,"n_rows":4,"n_cols":4,"rows_kept":4,"cut":false,"hidden":false,"merged":[[0,1,0,3],[1,1,1,3],[2,0,2,3]]}
["检查内容","检查模型中所有的族实例坐标是否重复"]
["方法","1，获取本层所有的族实例(FamilyInstance)；\n2，按坐标进行分组；\n3，遍历分组，检查中的实例个数是否大于1，大于表示坐标重复，否则不重复。"]
["共检查XXX条数据，未通过检查的如下"]
["族名称","ID","通过","备注（失败原因）"]

{"sheet":"参考-revit分类","index":14,"n_rows":18,"n_cols":1,"rows_kept":18,"cut":false,"hidden":false,"merged":[]}
["专用设备"]
["喷头"]
["安全设备"]
["家具"]
["常规模型"]
["护理呼叫设备"]
["数据设备"]
["机械设备"]
["火警设备"]
["灯具"]
["照明设备"]
["电气装置"]
["电气设备"]
["电话设备"]
["窗"]
["管件"]
["门"]
["风管管件"]

{"sheet":"参考-连接件对照表","index":15,"n_rows":227,"n_cols":10,"rows_kept":227,"cut":false,"hidden":false,"merged":[]}
["专业名称","专业编码","系统类名称","系统类编码","设备类名称","设备类编码","设备部件类名称","设备部件类编码","风连接件","水连接件"]
["给排水专业","WS","喷灌系统","SI","喷灌机组","SISU",null,null,null,"√"]
[{"$nulls":4},"喷灌喷头","SISN",null,null,null,"√"]
[{"$nulls":4},"喷灌控制器","SICU",null,null,null,"√"]
[null,null,"中水系统","RW","中水储水箱","RWWT",null,null,null,"√"]
[{"$nulls":4},"中水处理机组","RWTU",null,null,null,"√"]
[{"$nulls":4},"中水供水机组","RWSU",null,null,null,"√"]
[{"$nulls":4},"雨水收集设备","RWRC",null,null,null,"√"]
[null,null,"燃气系统","FG","燃气调压箱","FGPA"]
[{"$nulls":4},"液化石油气瓶","FGLP"]
[null,null,"生活给水系统","DW","生活给水储水箱","DWWT",null,null,null,"√"]
[{"$nulls":4},"生活给水紫外线消毒器","DWUS",null,null,null,"√"]
[{"$nulls":4},"生活给水水箱消毒器","DWTS",null,null,null,"√"]
[{"$nulls":4},"生活给水供水机组","DWSU",null,null,null,"√"]
[{"$nulls":4},"生活给水水泵","DWPP",null,null,null,"√"]
[null,null,"生活热水系统","DH","生活热水储水箱","DHWT",null,null,null,"√"]
[{"$nulls":4},"生活热水太阳能集热器","DHSC",null,null,null,"√"]
[{"$nulls":4},"生活热水水泵","DHHP",null,null,null,"√"]
[{"$nulls":4},"生活热水换热器","DHHE",null,null,null,"√"]
[{"$nulls":4},"生活热水辅热设备","DHHA",null,null,null,"√"]
[{"$nulls":4},"生活热水燃气热水器","DHGH",null,null,null,"√"]
[{"$nulls":4},"生活热水燃气锅炉","DHGB",null,null,null,"√"]
[{"$nulls":4},"生活热水燃油锅炉","DHFB",null,null,null,"√"]
[{"$nulls":4},"生活热水电热水器","DHEH",null,null,null,"√"]
[{"$nulls":4},"生活热水电锅炉","DHEB",null,null,null,"√"]
[{"$nulls":4},"生活热水燃煤锅炉","DHCB",null,null,null,"√"]
[{"$nulls":4},"生活热水空气源热泵","DHAH",null,null,null,"√"]
[null,null,"直饮水系统","DD","直饮水处理机组","DDTU",null,null,null,"√"]
[{"$nulls":4},"即时加热器","DDIH",null,null,null,"√"]
[null,null,"水景系统","WS","水景喷头","WSSN",null,null,null,"√"]
[{"$nulls":4},"水景灯具","WSLT"]
[{"$nulls":4},"水景控制器","WSCU"]
[{"$nulls":4},"水景循环过滤机组","WSCF",null,null,null,"√"]
[null,null,"泳池系统","WP","泳池循环过滤机组","WPCF",null,null,null,"√"]
[null,null,"给排水电伴热系统","WH","给排水伴热电缆","WHTC"]
[{"$nulls":4},"给排水伴热保温器","WHIB"]
[{"$nulls":4},"给排水伴热控制器","WHCU"]
[null,null,"给排水人防系统","WD","人防储水箱","WDWT",null,null,null,"√"]
[null,null,"污水处理系统","ST","化粪池","STST"]
[{"$nulls":4},"潜污泵","STSP",null,null,null,"√"]
[{"$nulls":4},"餐饮除油成套设备","STOR",null,null,null,"√"]
[{"$nulls":4},"污废水一体式提升机组","STLU",null,null,null,"√"]
[{"$nulls":4},"集水坑","STCP"]
["弱电专业","WE","多媒体信息发布系统","MI","播放器","MIPL"]
[{"$nulls":4},"多媒体主机","MIHT"]
[{"$nulls":4},"多媒体显示屏","MIDS"]
[{"$nulls":4},"自助终端机","MIST"]
[null,null,"本地网络系统","LN","路由器","LNRT"]
[{"$nulls":4},"服务器主机","LNHT"]
[{"$nulls":4},"硬件防火墙","LNHF"]
[{"$nulls":4},"交换机","LNEX"]
[{"$nulls":4},"无线AP点位","LNAP"]
[null,null,"车库管理系统","GM","车库网络控制器","GMNC"]
[{"$nulls":4},"机械车位","GMMP"]
[{"$nulls":4},"车库主机","GMHT"]
[{"$nulls":4},"进出闸机","GMGT"]
[{"$nulls":4},"车库显示屏","GMDS"]
[{"$nulls":4},"充电桩","GMCP"]
[{"$nulls":4},"车库摄像头","GMCM"]
[null,null,"建筑设备监控系统","BA","楼控网络控制器","BACU"]
[{"$nulls":4},"楼控主机","BAHT"]
[{"$nulls":4},"楼控控制面板","BACP"]
[null,null,"无线对讲系统","WT","中继台","WTRS"]
[{"$nulls":4},"对讲机","WTWT"]
[null,null,"电视信号系统","TV","电视前端设备","TVFE"]
["安防专业","SP","巡更系统","NP","巡更棒","NPPS"]
[{"$nulls":4},"巡更主机","NPHT"]
[{"$nulls":4},"巡更通讯座","NPCU"]
[null,null,"入侵报警系统","IA","入侵报警探测器","IASE"]
[{"$nulls":4},"入侵报警主机","IAHT"]
[null,null,"门禁系统","EG","速通门","EGFG"]
[{"$nulls":4},"门禁控制器","EGCU"]
[{"$nulls":4},"门禁读卡器","EGCR"]
[null,null,"视频监控系统","VS","监控主机","VSHT"]
[{"$nulls":4},"监控前端设备","VSFE"]
[{"$nulls":4},"硬盘录像机","VSDR"]
[{"$nulls":4},"监控摄像头","VSCM"]
[{"$nulls":4},"监视器","VSVM"]
["强电专业","SE","强电人防系统","SD"]
[null,null,"室外动力系统","OP"]
[null,null,"照明系统","LT","照明灯具","LTLT"]
[{"$nulls":4},"照明控制面板","LTCP"]
[null,null,"机房动力系统","EP"]
[null,null,"电梯系统","EL","电梯牵引机","ELET"]
[{"$nulls":4},"扶梯","ELES"]
[{"$nulls":4},"电梯救援设备","ELER"]
[{"$nulls":4},"直梯","ELEL"]
[null,null,"柴发机房系统","DG","柴油发电机","DGDG"]
[null,null,"备用电源系统","BP","风力发电装置","BPWG"]
[{"$nulls":4},"太阳能电池板","BPSP"]
[{"$nulls":4},"备用电源","BPBP"]
[null,null,"租户配电系统","TP","租户母线插接箱","TPBP"]
[null,null,"变配电系统","TD","变压器","TDTF"]
[{"$nulls":4},"低压开关柜","TDLS","低压配电抽屉","TDLSDW"]
[{"$nulls":4},"高压开关柜","TDHS","综合保护装置","TDHSIP"]
[{"$nulls":4},"直流屏","TDDS"]
[{"$nulls":4},"变配电母线插接箱","TDBP"]
["其他专业","OT","传感器系统","SE","温度传感器","SETP",null,null,null,"√"]
[{"$nulls":4},"速度传感器","SESP"]
[{"$nulls":4},"声音传感器","SESD"]
[{"$nulls":4},"湿度传感器","SERH"]
[{"$nulls":4},"压力传感器","SEPS",null,null,null,"√"]
[{"$nulls":4},"人流量传感器","SEPF"]
[{"$nulls":4},"热量传感器","SEHT"]
[{"$nulls":4},"流量传感器","SEFL",null,null,null,"√"]
[{"$nulls":4},"电度传感器","SEEE"]
[{"$nulls":4},"位移传感器","SEDP"]
[{"$nulls":4},"浓度传感器","SECT"]
[{"$nulls":4},"组合式传感器","SECB"]
[{"$nulls":4},"图像传感器","SEVD"]
[null,null,"管网系统","PW","液体管道","PWLQ"]
[{"$nulls":4},"气体管道","PWGS"]
[{"$nulls":4},"弱电线路","PWWE"]
[{"$nulls":4},"强电线路","PWSE"]
[null,null,"执行器系统","AE","安全阀","AESV",null,null,null,"√"]
[{"$nulls":4},"减压阀","AERV",null,null,null,"√"]
[{"$nulls":4},"继电器","AERL"]
[{"$nulls":4},"通断阀","AEOV",null,null,null,"√"]
[{"$nulls":4},"变频器","AEFC",null,null,null,"√"]
[{"$nulls":4},"止回阀","AECV",null,null,null,"√"]
[{"$nulls":4},"调节阀","AEAV",null,null,null,"√"]
[null,null,"其他系统","XX","其他设备","XXXX"]
[null,null,"工具系统","TL"]
["消防专业","FF","防排烟系统","SC","防火排烟阀","SCSD",null,null,"√"]
[{"$nulls":4},"排烟风口","SCIO",null,null,"√"]
[{"$nulls":4},"防排烟风机","SCEF",null,null,"√"]
[null,null,"气体灭火系统","GE","气体灭火控制器","GECU"]
[{"$nulls":4},"气体灭火瓶组","GEBG"]
[{"$nulls":4},"气体灭火喷头","GESN"]
[{"$nulls":4},"气体灭火启动瓶","GESB"]
[null,null,"燃气报警系统","GA","燃气探测器","GASE"]
[{"$nulls":4},"燃气报警主机","GAHT"]
[{"$nulls":4},"燃气切断阀","GACV",null,null,null,"√"]
[null,null,"消防给水系统","FS","湿式报警阀组","FSWV",null,null,null,"√"]
[{"$nulls":4},"消防水箱","FSWT",null,null,null,"√"]
[{"$nulls":4},"消防水炮设备","FSWM",null,null,null,"√"]
[{"$nulls":4},"消防伴热电缆","FSTC"]
[{"$nulls":4},"喷淋供水加压泵","FSSP",null,null,null,"√"]
[{"$nulls":4},"预作用报警阀组","FSPV",null,null,null,"√"]
[{"$nulls":4},"消防稳压设备","FSPS",null,null,null,"√"]
[{"$nulls":4},"水泵接合器","FSPC",null,null,null,"√"]
[{"$nulls":4},"室外消火栓","FSOH",null,null,null,"√"]
[{"$nulls":4},"水喷雾供水加压泵","FSMP",null,null,null,"√"]
[{"$nulls":4},"消火栓供水加压泵","FSHP",null,null,null,"√"]
[{"$nulls":4},"消火栓箱","FSHB",null,null,null,"√"]
[{"$nulls":4},"泡沫储罐组","FSFT",null,null,null,"√"]
[{"$nulls":4},"末端试水装置","FSET",null,null,null,"√"]
[{"$nulls":4},"干式报警阀组","FSDV",null,null,null,"√"]
[{"$nulls":4},"消火栓控制面板","FSCP"]
[{"$nulls":4},"停机坪消防供水加压泵","FSAP",null,null,null,"√"]
[{"$nulls":4},"空压机","FSAC"]
[null,null,"防火卷帘门系统","FR","防火卷帘门","FRFR"]
[{"$nulls":4},"防火卷帘门控制箱","FRCU"]
[{"$nulls":4},"防火卷帘门控制面板","FRCP"]
[null,null,"灭火器系统","FE","灭火器","FEFE"]
[null,null,"火灾报警系统","FA","火灾报警主机","FAHT"]
[{"$nulls":4},"火灾报警显示屏","FADS"]
[{"$nulls":4},"消防报警控制箱","FACU"]
[{"$nulls":4},"声光报警器","FAAL"]
[{"$nulls":4},"火灾探测器","FASE"]
[{"$nulls":4},"联动琴台","FALP"]
[null,null,"漏电火灾报警系统","EA","温度探测器","EATS",null,null,null,"√"]
[{"$nulls":4},"漏电探测器","EALS"]
[{"$nulls":4},"电流探测器","EAIS"]
[{"$nulls":4},"漏电火灾报警主机","EAHT"]
[null,null,"紧急广播及背景音乐系统","BM","广播前端设备","BMFE"]
[{"$nulls":4},"广播分区控制器","BMCU"]
[{"$nulls":4},"扬声器","BMSP"]
["空调专业","AC","厨房排油烟系统","KL","厨房风口","KLIO",null,null,"√"]
[{"$nulls":4},"油烟净化器","KLAP",null,null,"√"]
[{"$nulls":4},"厨房风机","KLSF",null,null,"√"]
[null,null,"中央供热系统","CH","供热集水器","CHCL",null,null,null,"√"]
[{"$nulls":4},"供热定压补水装置","CHCF",null,null,null,"√"]
[{"$nulls":4},"供热水加药装置","CHCD",null,null,null,"√"]
[{"$nulls":4},"供热燃煤锅炉","CHCB",null,null,null,"√"]
[{"$nulls":4},"供热真空脱气机","CHVD",null,null,null,"√"]
[{"$nulls":4},"供热全程水处理仪","CHTU",null,null,null,"√"]
[{"$nulls":4},"供热软化水装置","CHSD",null,null,null,"√"]
[{"$nulls":4},"供热水泵","CHHP",null,null,null,"√"]
[{"$nulls":4},"供热换热器","CHHE",null,null,null,"√"]
[{"$nulls":4},"供热燃气锅炉","CHGB",null,null,null,"√"]
[{"$nulls":4},"供热补水泵","CHFP",null,null,null,"√"]
[{"$nulls":4},"供热燃油锅炉","CHFB",null,null,null,"√"]
[{"$nulls":4},"供热电锅炉","CHEB",null,null,null,"√"]
[{"$nulls":4},"供热分水器","CHDB",null,null,null,"√"]
[null,null,"中央供冷系统","CC","供冷换热器","CCHE",null,null,null,"√"]
[{"$nulls":4},"供冷乙二醇泵","CCGP",null,null,null,"√"]
[{"$nulls":4},"地源热泵","CCGH","地埋管","CCGHBP",null,"√"]
[{"$nulls":4},"供冷补水泵","CCFP",null,null,null,"√"]
[{"$nulls":4},"供冷分水器","CCDB",null,null,null,"√"]
[{"$nulls":4},"供冷冷冻水泵","CCCP",null,null,null,"√"]
[{"$nulls":4},"供冷集水器","CCCL",null,null,null,"√"]
[{"$nulls":4},"供冷定压补水装置","CCCF",null,null,null,"√"]
[{"$nulls":4},"供冷水加药装置","CCCD",null,null,null,"√"]
[{"$nulls":4},"离心式冷水机组","CCCC",null,null,null,"√"]
[{"$nulls":4},"空气源热泵","CCAH",null,null,null,"√"]
[{"$nulls":4},"吸收式冷水机组","CCAC",null,null,null,"√"]
[{"$nulls":4},"水源热泵","CCWH",null,null,null,"√"]
[{"$nulls":4},"供冷真空脱气机","CCVD",null,null,null,"√"]
[{"$nulls":4},"供冷全程水处理仪","CCTU",null,null,null,"√"]
[{"$nulls":4},"蓄冷热槽","CCST",null,null,null,"√"]
[{"$nulls":4},"供冷软化水装置","CCSD",null,null,null,"√"]
[{"$nulls":4},"螺杆式冷水机组","CCSC",null,null,null,"√"]
[{"$nulls":4},"冷却塔","CCOT",null,null,null,"√"]
[{"$nulls":4},"供冷冷却水泵","CCOP",null,null,null,"√"]
[null,null,"空调末端系统","AT","散热器","ATRD",null,null,null,"√"]
[{"$nulls":4},"空调静压箱","ATPC",null,null,"√"]
[{"$nulls":4},"空调风口","ATIO",null,null,"√"]
[{"$nulls":4},"新风机组","ATFU",null,null,"√","√"]
[{"$nulls":4},"地板采暖设备","ATFH",null,null,null,"√"]
[{"$nulls":4},"风机盘管","ATFC",null,null,"√","√"]
[{"$nulls":4},"地板空调器","ATFA",null,null,"√"]
[{"$nulls":4},"空调机组","ATAH",null,null,"√","√"]
[{"$nulls":4},"变频多联机","ATVR",null,null,null,"√"]
[{"$nulls":4},"多联机室外机","ATVO",null,null,null,"√"]
[{"$nulls":4},"多联机室内机","ATVI",null,null,null,"√"]
[{"$nulls":4},"VAVBOX","ATVA",null,null,"√"]
[{"$nulls":4},"分体空调","ATSA"]
[null,null,"空调人防系统","AD","人防风机","ADSF",null,null,"√"]
[{"$nulls":4},"人防风口","ADIO",null,null,"√"]
[{"$nulls":4},"滤毒除湿机","ADFD",null,null,"√"]
[null,null,"通风系统","VT","通风风机","VTSF",null,null,"√"]
[{"$nulls":4},"通风风口","VTIO",null,null,"√"]
[{"$nulls":4},"除味装置","VTDO",null,null,"√"]
[{"$nulls":4},"风机控制面板","VTCP"]
[{"$nulls":4},"空气净化器","VTAP",null,null,"√"]
[{"$nulls":4},"热风幕","VTAC",null,null,null,"√"]

{"sheet":"参考-可识别的系统名称","index":16,"n_rows":132,"n_cols":2,"rows_kept":132,"cut":false,"hidden":false,"merged":[[0,1,7,1]]}
["循环供水","系统自带的"]
["循环回水"]
["其他"]
["其他消防系统"]
["卫生设备"]
["家用冷水"]
["家用热水"]
["干式消防系统"]
["冷、热水供水管"]
["冷、热水回水管"]
["冷却水供水管"]
["冷却水回水管"]
["雨水管"]
["污水管"]
["废水管"]
["通气管"]
["空调排风风管"]
["空调送风风管"]
["通风送风风管"]
["强电桥架"]
["消防桥架"]
["生活热水供水管"]
["生活热水回水管"]
["补风管"]
["排油烟管"]
["软化水管"]
["湿式消防系统"]
["预作用消防系统"]
["纯水管"]
["蒸汽凝结水管"]
["高压细水雾管"]
["医用气体-氧气管道"]
["医用气体-氮气管道"]
["医用气体-麻醉废气管道"]
["蒸汽管"]
["膨胀补水定压管"]
["地暖供水管"]
["市政热水供水管"]
["热媒供水管"]
["Hot and cold water supply pipes"]
["Hot and cold water return pipes"]
["Cooling water supply pipe"]
["Cooling water return pipe"]
["rain water pipe"]
["sewage pipe"]
["waste pipe"]
["breather pipe"]
["exhaust duct of air conditioner"]
["Air supply system of air conditioner"]
["Air supply system of ventilation"]
["Cable Tray of strong current"]
["Cable Tray of fire protection"]
["Domestic hot water supply pipe"]
["Domestic hot water return pipe"]
["air - makeup system"]
["Lampblack system"]
["Softening water pipe"]
["Wet fire protection system"]
["Pre-acting fire protection system"]
["pure water"]
["Steam condensing pipe"]
["High pressure water mist pipe"]
["Medical gas - oxygen pipe"]
["Medical gas - nitrogen gas pipe"]
["Medical gas - anesthetic exhaust pipe"]
["steam pipe"]
["Expansion water supply constant pressure pipe"]
["Floor heating water supply pipe"]
["Municipal hot water supply pipe"]
["Heat media supply pipe"]
["冷冻水供水管"]
["冷冻水回水管"]
["喷淋管"]
["膨胀水管"]
["冷凝水管"]
["消防供水管"]
["新风风管"]
["排烟风管"]
["回风风管"]
["弱电桥架"]
["通风排风风管"]
["给水管"]
["排水管"]
["供暖热水供水管"]
["供暖热水回水管"]
["排风兼排烟管"]
["正压送风风管"]
["直饮水管"]
["干式消防系统"]
["中水管"]
["酸性水管"]
["碱性水管"]
["医用气体-真空吸引管道"]
["医用气体-空气管道"]
["医用气体-二氧化碳管道"]
["补水管"]
["泄水管"]
["冷媒管"]
["地暖回水管"]
["市政热水回水管"]
["热媒回水管"]
["Chilled water supply pipe"]
["Chilled water return pipe"]
["spraying system"]
["Expansion Water Piping"]
["Condensate pipe"]
["Hydrant pipe"]
["Fresh air system"]
["smoke control system"]
["Air return system of air conditioner"]
["Cable Tray of weak current"]
["exhaust duct of air ventilation"]
["water supply system"]
["drainage system"]
["Heating hot water supply pipe"]
["Heating hot water return pipe"]
["Exhaust air and smoke exhaust system"]
["Positive pressure supply duct"]
["direct drinking water system"]
["Dry fire protection system"]
["reclaimed water"]
["acidic water"]
["alkaline water"]
["Medical gas - vacuum suction pipe"]
["Medical gas - air duct"]
["Medical gas - carbon dioxide pipe"]
["water supply pipe"]
["water drain pipe"]
["refrigerant liquid pipe"]
["Warm the return pipe to the floor"]
["Municipal hot water return pipe"]
["Heat media return pipe"]

{"sheet":"参考-管网及相关设备","index":17,"n_rows":37,"n_cols":6,"rows_kept":37,"cut":false,"hidden":false,"merged":[[11,4,12,4],[15,1,22,1],[34,0,35,0],[0,0,1,5],[15,2,22,2],[23,0,33,0],[23,1,27,1],[23,2,27,2],[28,1,30,1],[28,2,30,2],[3,0,22,0],[3,1,14,1],[3,2,14,2],[3,4,4,4],[5,4,6,4],[7,4,8,4],[9,4,10,4]]}
["管网及相关设备统计表"]
[]
["专业","分项","系统","系统类型","相关设备","备注"]
["空调专业",1.1000000000000001,"空调水系统","冷冻水供水管","CCCC-离心式冷水机组，CCAC-吸收式冷水机组，CCSC-螺杆式冷水机组，CCGH-地源热泵，CCWH-水源热泵，CCAH-空气源热泵，CCCP-供冷冷冻水泵，ATFC-风机盘管，ATAH-空调机组，ATFU-新风机组，CCHE-供冷换热器，CCAD-供冷软化水装置，CCCL-供冷集水器，CCDB-供冷分水器"]
[null,null,null,"冷冻水回水管"]
[null,null,null,"空调热水供水管","CHCB-供热燃煤锅炉，CHHE-供热换热器，CHGB-供热燃气锅炉，CHEB-供热电锅炉，CCGH-地源热泵，CCWH-水源热泵，CCAH-空气源热泵，CHHP-供热水泵，CHDB-供热分水器，CHCL-供热集水器，CHCF-供热定压补水装置,ATFC-风机盘管，ATAH-空调机组，ATFU-新风机组，CHTU-供热全程水处理仪，CHHE-供热换热器，CHWT-供热水箱，ATRD-散热器"]
[null,null,null,"空调热水回水管"]
[null,null,null,"供暖热水供水管","CHCB-供热燃煤锅炉，CHHE-供热换热器，CHGB-供热燃气锅炉，CHEB-供热电锅炉，CCGH-地源热泵，CCWH-水源热泵，CCAH-空气源热泵，CHHP-供热水泵，CHDB-供热分水器，CHCL-供热集水器，CHCF-供热定压补水装置,ATFC-风机盘管，ATAH-空调机组，ATFU-新风机组，CHTU-供热全程水处理仪，CHHE-供热换热器，CHWT-供热水箱，ATFC-风机盘管，ATAH-空调机组，ATFU-新风机组，ATRD-散热器"]
[null,null,null,"供暖热水回水管"]
[null,null,null,"冷、热水供水管","ATFU-风机盘管，ATAH-空调机组，ATFU-新风机组，CHVD-真空脱气机"]
[null,null,null,"冷、热水回水管"]
[null,null,null,"冷却水供水管","CCCC-离心式冷水机组，CCAC-吸收式冷水机组，CCSC-螺杆式冷水机组，CCGH-地源热泵，CCWH-水源热泵，CCAH-空气源热泵，CCOT-冷却塔，CCOP-冷却水泵"]
[null,null,null,"冷却水回水管"]
[null,null,null,"冷凝水管","ATFC-风机盘管"]
[null,null,null,"冷媒管","ATVI-室内机，ATVO-室外机"]
[null,1.2,"空调风系统","补风管","VTSF-送风风机，ATVA-VAVBOX "]
[null,null,null,"送风风管","VTSF-送风风机，ATVA-VAVBOX ,ATFC-风机盘管"]
[null,null,null,"排风风管","VTSF-排风风机"]
[null,null,null,"新风风管","ATFU-新风机组，ATAH-空调机组"]
[null,null,null,"排烟风管","ATVF-排烟风机"]
[null,null,null,"排风兼排烟管","VTSF-排风风机，VTSF-排烟风机"]
[null,null,null,"排油烟管","VTSF-抽油烟机"]
[null,null,null,"回风风管","ATFC-风机盘管，ATAH-空调机组"]
["给排水专业",2.1,"给水系统","给水管","DWHP-给水水泵，DWSU-生活给水供水机组，SEFL-水表，DWWT-水箱，DWPT-生活给水压力罐，CCOT-冷却塔"]
[null,null,null,"生活热水供水管","DHWT-生活热水储水箱，DHSC-生活热水太阳能集热器，SEFL-水表,DHHE-生活热水换热器"]
[null,null,null,"生活热水回水管","SEFL-水表"]
[null,null,null,"中水管","RWWT-中水储水箱，RWTU-中水处理机组，RWSU-中水供水机组，RWRC-雨水收集设备"]
[null,null,null,"高压细水雾管","高压微雾主机"]
[null,2.2000000000000002,"排水系统","污水管","STSP-潜污泵"]
[null,null,null,"废水管","STOS-自动隔油装置，STSP-潜污泵 "]
[null,null,null,"通气管"]
[null,2.2999999999999998,"中水系统","中水管"]
[null,2.4,"雨水系统","雨水管","雨水斗"]
[null,2.5,"直饮水系统","直饮水管","DDTU-直饮水处理机组，DDIH-即时加热器"]
["消防水",3.1,"喷淋系统","喷淋管","FSSP-喷淋供水加压水泵，FSPS-消防稳压装置"]
[null,3.2,"消防栓系统","消防供水管","FSHP-消火栓供水加压水泵，FSPS-消防稳压装置，FSHB-消火栓箱，FSWM-消防水炮设备"]
["其它"]